Water Supply

(August/September 1999)

Operations Group

(August/September)

Operations Group

Review of Operations

For the Period Ended 30 September 1999

1.	Items of Note

The optimisation trials at Te Marua and Wainuiomata are continuing to produce encouraging results.  Full scale trials at Te Marua have been successful, proving that the plant will operate in revised mode with blends of lake and river flows.  The spring algae bloom in one lake has proved more difficult to treat, resulting in reduced filter run times.  More research is necessary on this phenomena.

Major problems occurred at Waterloo where the variable speed drives to the newly installed Wellington pumps failed on four occasions.  The suppliers believe that they have now resolved the problem and carried out modifications to all three drives.

2.	Water Quality

A total of 686 samples from trunk mains were tested for coliform organisms.  None of these samples tested positive.

Secchi disc water clarity in the Te Marua north lake varied between 2.9 m.6 and 6.0 m, and in the south lake between 6.6 and 9.7 m.  These are considered satisfactory.  The dominant phytoplankton were as follows:

- North Lake: Oscillatoria, Synedra, Asterionella, Peridinium, Ankistrodesmus

- South Lake: Staurastrum, Synedra, Peridinium, Cosmarium and Cyclotella

When present in high concentrations Oscillatoria may cause filter clogging and Staurastrum may cause taste and odour in treated water.

Dissolved oxygen and pH readings are also satisfactory.

Twenty-two water samples were tested for Giardia and Cryptosporidium.  The results were as follows:

Te Marua

Treated water			)	nil detected

Lakes				)	nil detected

Intake				)	low level of Giardia, no Cryptosporidium detected

Wainuiomata

Treated Water			)	Nil detected

Orongorongo River intake	)	Low level of Giardia and Cryptosporidium detected

Big Huia intake 		)	Low level of Giardia.  No Cryptosporidium detected

Wainuiomata River intake	) 	Low level of Giardia.  No Cryptosporidium detected.

Lower George Creek intake	)	Low level of Giardia.  No Cryptosporidium detected.

Upper George Creek intake	)	Low level of Giardia.  No Cryptosporidium detected.

Over the August/September period 67 transgressions were notified:

- 4 low pH

- 8 high pH

- 12 low chlorine residual

- 25 low fluoride

- 4 high fluoride

- 7 high alkalinity

- 5 high turbidity

- 1 coliforms presumptive

- 1 coliforms confirmed

Seven artesian samples were tested for the presence of macro-organisms this month.  None were detected.  This testing is necessary to prove security of the groundwater.

3.	Supply Situation

The two monthly seasonal forecasts for September and October 1999 issued by the Meteorological Service is as follows:

Situation as at 9 September for Wellington:

Rain: 			Patchy and as likely to be above as below normal.

Wind: 			Slightly less than normal

Temperature: 	Continuing about 1 degree above normal

Sunshine: 		Average

Specials: 		Some thundery showers in Wellington and Wairarapa with the onset of southerly outbreaks

Confidence: 		Moderate to high

The northwesterly gales of spring are occurring but not as intensely as last year.  Regular cold fronts are expected to bring showery conditions rather than long periods of rain.

Hutt River Flows

The mean monthly river flow for the month of September was below average.

The monthly mean flows are show below.

Wainuiomata River Flows

The river flows for the month of September were below average.

Aquifer Levels

4.	Production

4.1	Te Marua

# 4.1.1	Quality

18 August:	High treated water alkalinity because of plant trials.  Process adjusted to maintain correct levels.

4.1.2	Safety

No safety incidents or accidents to report.

4.1.3	Operations

24/26 August:		Plant was shut down to allow maintenance of Hutt pipeline by the Distribution Section.

3 September:		Plant slam shut because of minor chlorine leak caused by faulty drum valve on empty cylinder.

15 September:		The recently installed CO2 leak detection system was activated by a gas leak from a loose connection on the carbonator.  This is the first time the system has operated in response to a real leak and it proved to work very well in avoiding a potentially lethal situation.

Plant Tours

12 August:		12 students from Wellington School of Medicine.

25 August:		18 staff on Wellington Regional Council induction tour.

27 August:		11 Massey University students.

4.1.4	Projects

Capital Works

Work has commenced on the installation of the standby generator at the pumping station.

Plant trials are almost complete.

4.2	Wainuiomata

4.2.1	Quality

Fluoride plant modifications have greatly improved reliability and reduced transgressions because of high/low fluoride levels.

4.2.2	Safety

No safety incidents or accidents to report.

4.2.3	Operations

19 August: 		The Orongorongo intake was put back into service after the all clear was given by the Health Officer following the 1080 drop.

23 August:		A large land slip partially dammed a contributory feeding into George Creek.  It is not feasible to remove the slip.  The current plan of attack is not to use this intake during any sign of rain, and hope that the annual October floods will clear the slip for us.

26 August:		The inverter for the Orongorongo Hydro Scheme failed.  This has been replaced.

31 August:		The slam shut valve hydraulic power unit failed, this was replaced within two days.  The plant continued to operate with semi manual control of the slam shut valve.

6 September: 		Initial results from filter DAF modifications indicate that backwash times have almost halved.

Plant Tours

31 August:		16 process engineers from Massey University.

13 September:		8 Environmental and Health Officer trainees.

17 September:		16 students on a water treatment course run by Massey University.

General

The optimisation of the plant operation is proceeding well, with initial indications identifying quite extensive savings and improvements possible in the quality of the treated water.

4.2.4	Projects

Capital Works

The Wainuiomata No. 3 Bridge strengthening project started on-site on the 24 September.

4.3	Waterloo

4.3.1	Quality

There were no quality issues to report.

4.3.2	Safety

No health and safety issues to report.

4.3.3	Operations

24 August:		Wellington Pump No. 2 variable speed drive failed during mid-August

4 September: 		Wellington Pump No. 3 variable speed drive failed.

6 September:		New control network commissioned which has produced more reliable and faster connection to Wainuiomata Water Treatment Plant.

Plant Tours

There were no plant tours during the period.

General

All five emergency standby diesel motors had their annual service.

The variable speed drives to the new installed Wellington pumps have failed on four occasions.  The supplier, Vectron Industries Ltd, has taken a drive up to their factory to investigate the failures further.  They have since found a fault and applied a solution to all the drives.  No further problems have been experienced to date.  The level of service and commitment shown by Vectron Industries Ltd has been very good.

4.3.4	Projects

Capital Works

Wellington pump upgrade – the Wellington pump bearing protection installation has commenced.

4.4	Gear Island

4.4.1	Quality

No quality issues to report.

4.4.2	Safety

No safety incidents or accidents to report.

4.4.3	Production

The plant has only been required intermittently during this period.

Plant Tours

No tours.

4.4.4	Projects

Capital Works

The new switchboard has been shop tested and is ready for delivery.  Installation is scheduled to commence on 11th October.

4.4.5	Operational Projects

During the switchboard installation shutdown three other projects will be undertaken.

- Removal and repair of DC Pump Motor No. 2.

- Removal of caustic bulk tank and strengthening of tank concrete plinth and fixings will be carried out to allow issuing of toxic substances licence.

- A corroded section of the main pump delivery main will be removed and repaired.

5.	Distribution

Electrical Section

New controls were fitted to the inlet valve at Plimmerton Reservoir to enable it to be remotely controlled.

The controls were also modified at Ascot Park Reservoir.

The new reservoir at Karori South (Makara) has been commissioned

Telemetry units have been installed at Mills Road and Dargle Way Pumping Stations.

Pipeline Section

# Te Marua to Karori Pipeline

- A new 600 mm line valve and bypass were installed in the 900 mm pipeline at Maoribank in Upper Hutt.

- A new 600 mm line valve and bypass were installed in the 900 mm pipeline at Moonshine Road.

- Four new scour valves were installed, complete with “non-return” valves.

Electromagnetic Flow Meters

- Installed a new electromagnetic flow meter at Manor Park.

1050 mm Main at Randwick

- There was a leak on the 1050 mm main near the Randwick valve chambers.

- The 1050 mm main between Tunnel Grove and Randwick were shut down to carry out a welding repair.

Karori Decommissioning

- Ongoing work with valving for the contractor.

Rahui Commissioning

- Ongoing work with pressurising the inlet main and filling the new Rahui Reservoir.

6.	Health and Safety

Total Injury/Illness/Incident Record

Production: 		Incident Free

Distribution:		Incident Free

Network		Two minor cuts with no time off.

Two minor sprains with no time off.

Operations Network

Review of Operations

## For the Period Ended 31 August 1999

1.	Items of Note

The number of damage repair jobs caused by subcontractors has reduced during the month.  This is of concern, as it is suspected that we are not receiving notification of all incidents when damage occurs.

There were nine mains burst during the month.  All were repaired within the time allocated under the performance targets.

2.	Water Supply (PT 30.1)

3.	Financial

3.1	Facilities Management Contract

Contract Amounts : Wellington, including Tawa

| Month | Actual $ | Budget $ | Variance % | Year To Date | Budget $ | Variance % |
| --- | --- | --- | --- | --- | --- | --- |
| August | 258,382 | 294,314 | -12.2% | 500,064 | 588,628 | -15.05 |

4.	Water Quality

Routine Testing  (PT 1.1)

The water quality was monitored and the appropriate laboratory tests were completed for the month of August.  There were 136 samples from the reticulation system tested for bacteriological compliance.  Compliance for the month is 100 percent.  Compliance for the year to date is 100 percent.

Water Tests Initiated by Customers (PT 2)

|  |  | August | Year to Date | Compliance (%) Year to Date |
| --- | --- | --- | --- | --- |
|  | Number received | 6 | 22 | - |
| (PT 2.2) | Within ability of Operations Network to control | 2 | 4 | - |
| (PT 2.1) | Formal response within five days | 6 | 20 | 91% |

5.	Customer Services

5.1	Counter and Other Office Services   (PT 3.1.)  (PT 4.1)  (PT 5.1)

An enquiry/complaints register is being maintained.  A breakdown of complaints and enquiries received during the reporting period is as follows:

|  | August |  |
| --- | --- | --- |
|  | Counter enquiries | 78 (+ 13 encroachments) |
|  | Proposals from other utilities | 15 |
| (PT 33.1) | Plan records: - New services recorded | 15 |
|  | Compliance with response time requirement | 100% |

5.2	Complaints Register (Monthly Summary)  (PT 5.1)

A complaints register is being maintained.  A breakdown of the complaints received during the reporting period is as follows:

|  | August |  |
| --- | --- | --- |
|  |  | Complaints |
| (PT 2.2) | Water quality | 6 |
| (PT 16.1.2) | Pressure | 9 |
| (PT 20.1) | Reinstatement | 0 |
| (PT 16.1.4) | No-water | 16 |
|  | Contractors | 1 |
|  | Other | 0 |

All of the “Pressure” and “Water Quality” complaints were responded to and completed within the performance criteria.  Fourteen of the 16 no-water calls regarding “Supply” were attended within 30 minutes as required by the Facilities Management Contract.  (The two no--water calls which have failed were attended late by a maximum of 10 minutes.)

6.	Response Maintenance

6.1	Compliance

|  |  | August |  |  |
| --- | --- | --- | --- | --- |
|  |  | Number of Calls | Completed to Standard | Compliance % |
| (PT 9.1) | Stopcocks | 347 | 333 | 96% |
| (PT 9.1) | Hydrants | 89 | 85 | 96% |
| (PT 9.1a) | Valves | 19 | 16 | 84% |
| (PT 9.2) | Other Leaks | 241 | 225 | 93% |
| (PT 10.1) | Mark-outs | 51 | 51 | 100% |
| (PT9.1a) | Value Repacks | 45 | 10 | 22% |
| (PT 16.1.1) | Burst mains | 9 | 9 | 100% |
| (PT 2.1) | Water Quality Complaints | 6 | 6 | 100% |
|  |  | 807 | 735 | 91% |

It is noted that the compliance figures for valve repacks is very low.  The majority of these valve leaks were suppressed but still needed to be repacked.  Because they were not leaking, we were not in a position to give them a higher priority than actual leaks.  Since we have managed to control the number we now have, it is expected that the compliance figure will increase substantially over the next 2-3 months.

Additional Work Carried Out

New Services		8

Damages by Contractors	34

6.2	Burst Mains  (PT 16.1)

There were a total of nine burst mains during the month August 1999.  They were as follows:

Tyers Road (Online Security)	1 August 1999

12 Earp Street, Johnsonville	4 August 1999

58 Standen Street, Karori	5 August 1999

1 Ryan Grove, Tawa		9 August 1999

Cnr Donald Street and Ellerton Way	8 August 1999

3 Ridd Crescent, Karori	7 August 1999

15 Ranelagh Street, Karori	8 August 1999

15 Franklyn Road, Tawa	11 August 1999

99 Helston Road, Newlands	20 August 1999

All of the burst mains were attended to within 30 minutes and repaired within eight hours.

  - Supply  (PT 16.1)

|  | August |
| --- | --- |
| Total calls received regarding loss of or temporary loss of supply because of broken mains or supply failure | 16 |
| Total calls attended within 30 minutes | 14 |
| Total Compliance | 88% |

6.4	Reinstatement  (PT 20.1)

There were no complaints received this month regarding trench reinstatements.  The Facilities Management Contract target is less than 12.

6.5	Shutdown Notification  (PT 6.1)

There were 15 planned shutdowns during August 1999.  All identifiable customers received notification within 24 hours prior to the shutdown.

6.6	Locates and Investigations  (PT 10.1)

Work completed during the month comprised:

|  | August |
| --- | --- |
| Locate stopcocks | 85 |
| Leak location | 70 |
| Flow tests | 0 |
| Seepage/Investigations | 1 |
| Miscellaneous supply jobs | 7 |

7.	Health and Safety

There were four minor incidents reported this month.  There was one serious car accident where one of our staff suffered a broken arm.

8.	Meters (PT 13.1)

A total of 1,315 city and high use meters were read and entered into the system by 23 August 1999.

9.	Pumping Stations, Reservoirs and System Control

9.1	General

Normal routine maintenance has resulted in the Wellington City system operating satisfactorily.

  - Control System (PT 30.1)

The control system continues to operate satisfactorily.

9.3	Burnside Reservoir and Pumping Station

Telemetry units have been installed at Burnside Reservoir and Burnside Pumping Station.  The pumping station has been modified and is now controlled from the telemetry.

9.4	Karori Pumping Station

At Karori Pumping Station a pump bearing was replaced on the Kelburn pump.

9.5	Dargle Way and Mills Road Pumping Stations

Remote telemetry units have been installed at Dargle Way Pumping Station and at Mills Road Pumping Station.  The pump at Mills Road Pumping Station is now controlled from the pressure transmitter.  The pump pressure has been raised, but there are still complaints of pressure fluctuations from 163 Washington Avenue.  This is being investigated.

9.6	Lyndhurst Pumping Station

The electric motor on No. 2 pumpset burnt out.  It has been rewound by a contractor, reinstalled and put back into service.

9.7	Broderick Road Pumping Station

The No. 1 pumpset has been removed and taken to the local agents for a major overhaul.

9.8	Maintenance Checks  (PT 17.4)

Maintenance has been carried out as follows:

| August |  |
| --- | --- |
| Round A | Round B |
| Allington Road Messines Road Pumping Station Karori Park Montgomery Avenue Makara Road Verviers Street The Zoo Russell Terrace Lyndhurst Road/Chester Mills Road Baylands CV Omega CV Woodridge CV Sidlaw Street CV | Karepa Street Highbury Carries Gully Landfill Pump Rhine Street Beacon/Signal Hill Townsend Road Miramar North Dargle Way Grenada CV Rangoon Heights CV Ngaio CV Cunliffe CV Cambrian CV |

10.	Development

10.1	Development Statistics

| Subdivisions | August | Year to Date |
| --- | --- | --- |
| Construction plans approved (lots/units) | 2 | 2 |
| Scheme plans approved | 36 | 71 |
| Subdivisions cleared (lots/units) | 43 | 92 |

10.2	Development Projects

10.2.1	Woodridge Reservoir

Hydroseeding and disconnection is being discussed.

10.2.2	Churton North Reservoir

Construction of the reservoir is underway.  The floor and walls have been built.  Two roof beams are in place.

10.2.3	Westchester Drive Pumping Station

Pumps have been approved.  Building and layouts are being approved.

10.2.4	Major Subdivisions

Construction plans for the following subdivisions were submitted and approved as follows:

Bellevue Lands		Stage 6, Newlands

142 Ghuznee Street		3 lots, 10 units

As-built plans for one major subdivision was submitted and approved.

Takapu  Road – Stage 2	15 lots, as built approval

10.2.5	Fire Services

| Fire Services Recently Priced (PT 12.1) | Fire Services Recently Connected |
| --- | --- |
| 80 Salamanca Road |  |

10.2.6	Domestic Services

| Domestic Services Priced | Domestic Services (PT12.2) Recently Connected |
| --- | --- |
| 124 Owhiro Bay Parade 108 Ashton Fitchett Drive | 48 Aro Street 12-14 Atua Street 62 Chesterton Street 92-94 Calabar Road 72 Derwent Street 74 Dress Circle 60 Freyberg Street 17 Furlong Crescent 33-39 Johnsonville Road 27 Kanpur Road 27 Kabul Street 21 Mahora Street 38 Ottawa Road 99 The Parade 138-140 Park Road 80 Salamanca Road 1 Tyers Road 2-6 Tobago Crescent 139 The Parade Wilton Road (Otari Reserve) |

10.3	Building Development Appraisals

|  | ### August |  |
| --- | --- | --- |
|  | Commercial | Domestic |
| Building consents | 10 | 55 |
| PIMS applications | 10 | 60 |
| Compliance with response time requirement | 100% | 100% |

10.4	Land Information Memoranda

| August |  |
| --- | --- |
| Applications processed | 29 |
| Compliance with response time requirement | 100% |

11.	Capital Works

11.1	Main Laying City

11.1.1	Contracts in Maintenance Period

The Terrace pipe replacement contract is in the maintenance period.

The maintenance periods for Courtenay Place, Marion Street and Hall and Riddiford Streets Contracts have expired.  Arrangements are being made to rectify any minor maintenance issues and to release the maintenance retentions.

11.1.2	Taranaki Street

Investigations into replacement of the 150 mm cast iron main in Taranaki Street are on hold.

A report has been prepared and submitted to Wellington City Council on the condition of two short pieces of pipe removed from the main.

11.2	Main Laying Suburbs

11.2.1	Contracts in Maintenance Period

The following pipelaying contracts are in the maintenance period:

- Johnsonville Road

- Tirangi, McGregor, Kingsford Smith and George Bolt Streets

- Bracken Road

- Breaker Bay Road

The maintenance periods for Miles Crescent/Lyndfield Lane, Chelmsford Street and Rakau Road, Hapua Street and Upoko Road Contracts have expired.  Arrangements are being made to rectify any minor maintenance issues and to release the maintenance retentions.

11.2.2	Owhiro Bay Parade

The Contract for replacing the pipeline along Owhiro Bay Parade was awarded to Pipeline Techniques.  Approximately 300 m of pipe has been installed.

11.2.3	Helston Road, Newlands

The Contract for replacing the pipeline along Helston Road was awarded to Groundworks Ltd.  The pipelaying has been completed and connections are now being made.

11.2.4	Rider Mains Replacement

The Contract for the replacement of rider mains was awarded to N Forsyth Ltd.  The Contractor has installed new rider mains in Somerville Terrace, Richmond Avenue, Queens Drive and Nikau and Derwent Streets.  The rider main has been laid in Ruahine Street and connections are about to be made.  Work is about to start on Moxham Avenue.

11.3	High Level Distribution and Storage

11.3.1	Karori South Reservoir

The Contract for the construction of the reservoir attained Practical Completion on 14 August 1999.  The reservoir is in service.  Planning for supplying the Allington Road Zone from the new reservoir is underway.

11.3.2	Makara Road Rising Main

The Contract for installing a rising main to the new Karori South Reservoir was awarded to N Forsyth Ltd.  Approximately 200 m of pipe has been installed.

11.3.3	Wadestown Reservoir

Montgomery Watson Ltd is undertaking the design and making arrangements to obtain resource consents for the proposed reservoir.  The draft Assessment of Environmental Effects is almost complete.

The application for the resource consents is about to be made.  A public meeting was held with the local residents and Friends of the Town Belt.

11.4	Low Level Zone Storage

11.4.1	Eastern Suburbs Storage Enhancement

Investigations into the potential sites and proposed level for this reservoir have been completed.  A draft report presenting the results of this investigation has been prepared and reviewed.  The final report is being prepared.

| Analysis - December 1998 to August 1999 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Stopcocks |  |  | Toby Locates | Damage Repairs | Burst Mains |  | Leaks |  |  | Total Calls |  |  | Mark-outs |  |
|  | Calls Received | Completed | % Comp |  |  | Occurred | % Comp | Calls Received | Completed | % Comp | Received | Completed | % Comp | Received | % Comp |
| December 1998 | 365 | 362 | 99% | 101 | 26 | 4 | 100% | 234 | 233 | 99% | 770 | 763 | 99% | 16 | 100% |
| January 1999 | 431 | 429 | 99% | 92 | 23 | 7 | 100% | 275 | 271 | 98% | 875 | 868 | 99% | 21 | 100% |
| February 1999 | 343 | 336 | 97% | 100 | 29 | 5 | 100% | 176 | 170 | 96% | 647 | 630 | 97% | 11 | 100% |
| March 1999 | 488 | 359 | 74% | 102 | 102 | 8 | 100% | 324 | 282 | 84% | 1073 | 884 | 82% | 108 | 100% |
| April 1999 | 430 | 367 | 85% | 64 | 46 | 7 | 100% | 259 | 221 | 85% | 945 | 831 | 88% | 94 | 100% |
| May 1999 | 366 | 285 | 78% | 81 | 109 | 2 | 100% | 239 | 200 | 84% | 875 | 729 | 83% | 140 | 100% |
| June 1999 | 364 | 269 | 74% | 80 | 105 | 7 | 100% | 262 | 204 | 77% | 837 | 655 | 78% | 86 | 100% |
| July 1999 | 385 | 345 | 90% | 91 | 75 | 8 | 100% | 267 | 258 | 96% | 830 | 767 | 92% | 47 | 100% |
| Aug ust1999 | 347 | 333 | 96% | 85 | 34 | 9 | 100% | 241 | 225 | 98% | 807 | 735 | 91% | 51 | 100% |

Operations Network

Review of Operations

## For the Period Ended 30 September 1999

1.	Items of Note

During the month nine burst mains occurred, all were attended to within 30 minutes and repaired within eight hours.

The number of damage repairs caused by subcontractors has continued to cause concern, with 54 incidents occurring during the month.

2.	Water Supply (PT 30.1)

3.	Financial

3.1	Facilities Management Contract

Contract Amounts : Wellington, including Tawa

| Month | Actual $ | Budget $ | Variance % | Year To Date | Budget $ | Variance % |
| --- | --- | --- | --- | --- | --- | --- |
| September | 235,123 | 294,314 | -20.11% | 735,187 | 882,942 | -16.73% |

4.	Water Quality

Routine Testing (PT 1.1)

The water quality was monitored and the appropriate laboratory tests were completed for the month of September.  There were 136 samples from the reticulation system tested for bacteriological compliance.  Compliance for the month is 100 percent.  Compliance for the year to date is 100 percent.

Water Tests Initiated by Customers (PT 2)

|  |  | September | Year to Date | Compliance (%) Year to Date |
| --- | --- | --- | --- | --- |
|  | Number received | 1 | 23 | - |
| (PT 2.2) | Within ability of Operations Network to control | 0 | 4 | - |
| (PT 2.1) | Formal response within five days | 0 | 20 | 87% |

5.	Customer Services

5.1	Counter and Other Office Services   (PT 3.1.)  (PT 4.1)  (PT 5.1)

An enquiry/complaints register is being maintained.  A breakdown of complaints and enquiries received during the reporting period is as follows:

|  | September |  |
| --- | --- | --- |
|  | Counter enquiries | 69 |
|  | Proposals from other utilities | 14 |
| (PT 33.1) | Plan records: - New services recorded | 23 |
|  | Compliance with response time requirement | 100% |

5.2	Complaints Register (Monthly Summary)  (PT 5.1)

A complaints register is being maintained.  A breakdown of the complaints received during the reporting period is as follows:

|  | September |  |
| --- | --- | --- |
|  |  | Complaints |
| (PT 2.2) | Water quality | 1 |
| (PT 16.1.2) | Pressure | 12 |
| (PT 20.1) | Reinstatement | 1 |
| (PT 16.1.4) | No-water | 50 |
|  | Contractors | 1 |
|  | Other | 7 |

All of the “Pressure” and “Water Quality” complaints were responded to and completed within the performance criteria.

6.	Response Maintenance

6.1	Compliance

|  |  | September |  |  |
| --- | --- | --- | --- | --- |
|  |  | Number of Calls | Completed to Standard | Compliance % |
| (PT 9.1) | Stopcocks | 356 | 275 | 77% |
| (PT 9.1) | Hydrants | 72 | 68 | 94% |
| (PT 9.1a) | Valves | 20 | 18 | 90% |
| (PT 9.2) | Other Leaks | 276 | 226 | 82% |
| (PT 10.1) | Mark-outs | 41 | 41 | 100% |
| (PT9.1a) | Value Repacks | 2 | 2 | 100% |
| (PT 16.1.1) | Burst mains | 9 | 9 | 100% |
| (PT 2.1) | Water Quality Complaints | 1 | 1 | 100% |
|  |  | 777 | 640 | 82% |

Additional Work Carried Out

New Services		7

Damages by Contractors	54

6.2	Burst Mains (PT 16.1)

There were a total of nine burst mains during the month September 1999.  They were as follows:

Cnr Ironside Ohariu Roads, Johnsonville	3September 1999

17 Ironside Road, Johnsonville	5 September 1999

2b Bushland Grove, Johnsonville	6 September 1999

Helston Road, Johnsonville	6 September 1999

Cnr Burgess Road and Macaulay Avenue, Johnsonville	6 September 1999

124 Helston Road, Newlands	8 September 1999

110 Oxford Street, Tawa	14 September 1999

98 Owhiro Bay Parade, Happy Valley	19 September 1999

Duthie Street, Karori	21 September 1999

All of the burst mains were attended to within 30 minutes and repaired within eight hours.

6.4	Supply (PT 16.1)

|  | September |
| --- | --- |
| Total calls received regarding loss of or temporary loss of supply because of broken mains or supply failure | 50 |
| Total calls attended within 30 minutes | 50 |
| Total Compliance | 100% |

6.4	Reinstatement (PT 20.1)

There was one complaint received this month regarding trench reinstatements.  The Facilities Management Contract target is less than 12.

6.5	Shutdown Notification (PT 6.1)

There were 12 planned shutdowns during September 1999.  All identifiable customers received notification within 24 hours prior to the shutdown.

6.6	Locates and Investigations (PT 10.1)

Work completed during the month comprised:

|  | September |
| --- | --- |
| Locate stopcocks | 75 |
| Leak location | 56 |
| Flow tests | 0 |
| Seepage/Investigations | 1 |
| Miscellaneous supply jobs | 13 |

7.	Health and Safety

There were six minor incidents reported this month.

8.	Meters (PT 13.1)

A total of 1,400 suburb and high use meters were read and entered into the system by 23 September 1999.

9.	Pumping Stations, Reservoirs and System Control

9.1	General

Routine maintenance resulted in the Wellington City system operating satisfactorily.

9.3	Control System (PT 30.1)

The control system continues to operate satisfactorily.

Telemetry units have been installed at the Burnside Reservoir and Burnside Pumping Station.  The pumping station is now controlled by the telemetry system.

9.3	Broderick Road Pumping Station

The No. 1 pumpset has been removed and sent to the agent for major refurbishment, and returned to service.

9.4	Grenada North High Reservoir

A mains power supply has been laid and connected to the TDI hut at Grenada North High Reservoir.  It was previously supplied by battery power.

9.5	Dargle Way and Mills Road Pumping Stations

Remote telemetry units have been installed at Dargle Way Pumping Station and Mills Road Pumping Station.

Mills Road Pumping Station is being controlled by the telemetry unit.

9.6	Lyndhurst Pumping Station

The electric motor on No. 2 pumpset burnt out. It has been rewound by a contractor, reinstalled, and commissioned by our staff.

9.7	Maintenance Checks  (PT 17.4)

Maintenance has been carried out as follows:

| September 1999 |  |
| --- | --- |
| Round E | Round F |
| Johnsonville Pumping Station Ngauranga Reservoir/Pumping Station Kaiwharawhara Pumping Station Thorndon Pumping Station Karori Reservoir/Pumping Station Macalister Park Reservoir Churton Park CV Maldive Reg/Abb CV Tawa Linden | Randwick Pumping Station Tunnel Grover Chamber Rocky Point Chamber Korokoro Valve Chamber Wainuiomata Pumping Station Moores Valley Pumping Station Mabey Road Generator Naenae Reservoir Gracefield Reservoir Rahui Reservoir Buick Street Pumping Station |

10.	Development

10.1	Development Statistics

| Subdivisions | September | Year to Date |
| --- | --- | --- |
| Construction plans approved (lots/units) | 0 | 2 |
| Scheme plans approved | 27 | 98 |
| Subdivisions cleared (lots/units) | 39 | 131 |

10.2	Development Projects

10.2.1	Woodridge Reservoir

Hydroseeding and disconnection being discussed.

10.2.2	Churton North Reservoir

Construction of the reservoir is underway.  The roof has been completed.  The valve chamber and pipework is being constructed.  The steel work is outstanding.

10.2.3	Westchester Drive Pumping Station

Building and layouts are being approved.

10.2.4	Major Subdivisions

Construction plans for the following major subdivisions were submitted and approved:

Neferton Way			6 lots

Punjab Street

As-built plans for three major subdivisions were submitted and approved as follows:

Mana Street			6 lots

Downing Street		8 lots

Onslow Road			3 lots

10.2.5	Fire Services Recently Connected (PT 12.1)

Nil

10.3	Building Development Appraisals

Building development appraisals are as follows:

|  | ### September |  |
| --- | --- | --- |
|  | Commercial | Domestic |
| Building consents | 12 | 41 |
| PIMS applications | 14 | 42 |
| Compliance with response time requirement | 100% | 100% |

10.4	Land Information Memoranda

| September |  |
| --- | --- |
| Applications processed | 39 |
| Compliance with response time requirement | 100% |

11.	Capital Works

11.1	Main Laying City

11.1.1	Contracts in Maintenance Period

The Terrace pipe replacement contract is in the maintenance period. The maintenance periods for the Courtenay Place and Marion Street Contracts have expired.  Arrangements are being made to rectify any minor maintenance issues and to release the maintenance retentions.

The maintenance retention on Hall and Riddford Streets has been released.

11.1.2	Taranaki Street

Investigations into replacement of the 150 mm cast iron main in Taranaki Street are on hold.   A report has been prepared and submitted to Wellington City Council on the condition of two short pieces of pipe removed from the main.

11.1.3	Manor Street

Investigation and design for the replacement of the 300 mm cast iron main from Willis Street to Cuba Street has started.

11.1.4	Cuba Street

Investigation and design for the replacement of the 200 mm cast iron and 100 mm asbestos cement main from Ghuznee to Webb Street has started.

11.2	Main Laying Suburbs

11.2.1	Contracts in Maintenance Period

The following pipelaying contracts are in the maintenance period.

- Johnsonville Road

- Tirangi, McGregor, Kingsford Smith and George Bolt Streets

- Bracken Road

- Breaker Bay Road

The maintenance periods for Miles Crescent/Lyndfield Lane, Chelmsford Street and Rakau Road, Hapua Street and Upoko Road Contracts have expired.  Arrangements are being made to rectify any minor maintenance issues and to release the maintenance retentions.

11.2.2	Owhiro Bay Parade

The Contract for replacing the pipeline along Owhiro Bay Parade was awarded to Pipeline Techniques.  The 200 mm and 150 mm diameter pipeline has been commissioned.  The Contractor is completing the replacement of the rider main at the western end of the Parade.

11.2.3	Helston Road, Newlands

The Contract for replacing the pipeline along Helston Road was awarded to Groundworks Ltd.  The pipelaying has been completed and connections are being completed.  In addition to the Contract Works, the main in Hardy Street has been replaced.

11.2.4	Rider Mains Replacement

The Contract for the replacement of rider mains was awarded to N Forsyth Ltd.  The Contractor has installed new rider mains in Somerville Terrace, Richmond Avenue, Queens Drive, Nikau Street, Derwent Street and Ruahine Street.  Work is continuing on replacing the rider main in Moxham Avenue.

11.2.5	Fox Street, Ngaio

Design and preparation of Contract Documents for the replacement of the 100 mm asbestos cement pipeline in Fox Street from Awarua Street to Vasanta Avenue has started.

11.3	High Level Distribution and Storage

11.3.1	Karori South Reservoir

The Karori South Reservoir is in service.  Planning for supplying the Allington Road Zone from the new reservoir is progressing.

11.3.2	Makara Road Rising Main

The Contract for installing a rising main to the new Karori South Reservoir attained Practical Completion on 15 September 1999 and has been commissioned.

11.3.3	Wadestown Reservoir

Montgomery Watson Ltd is undertaking the design and making arrangements to obtain resource consents for the proposed reservoir and associated earthworks.  The Assessment of Environmental Effects is complete.  The application for the resource consents has been lodged and was advertised on 29 September.  Submissions close 28 October 1999.  A display has been erected in the Wadestown Library.

11.4	Low Level Zone Storage

11.4.1	Eastern Suburbs Storage Enhancement

The report on the potential sites and proposed level for this reservoir has been completed and submitted to Wellington City Council.

| Analysis - July 98 to September 99 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Stopcocks |  |  | Toby Locates | Damage Repairs | Burst Mains |  | Leaks |  |  | Total Calls |  |  | Mark-outs |  |
|  | Calls Received | Completed | % Comp |  |  | Occurred | % Comp | Calls Received | Completed | % Comp | Received | Completed | % Comp | Received | % Comp |
| July 1998 | 371 | 359 | 96% | 81 | 91 | 6 | 100% | 231 | 213 | 95% | 791 | 753 | 95% | 61 | 95% |
| August 1998 | 304 | 243 | 87% | 89 | 100 | 2 | 100% | 216 | 183 | 85% | 703 | 613 | 81% | 74 | 100% |
| September 1998 | 289 | 211 | 73% | 97 | 98 | 8 | 100% | 219 | 183 | 84% | 683 | 553 | 81% | 74 | 100% |
| October 1998 | 385 | 293 | 76% | 72 | 57 | 5 | 100% | 216 | 147 | 68% | 795 | 605 | 76% | 67 | 100% |
| November 1998 | 421 | 382 | 90% | 89 | 103 | 9 | 90% | 228 | 198 | 86% | 838 | 751 | 90% | 91 | 100% |
| December 1998 | 365 | 362 | 99% | 101 | 26 | 4 | 100% | 234 | 233 | 99% | 770 | 763 | 99% | 16 | 100% |
| January 1999 | 431 | 429 | 99% | 92 | 23 | 7 | 100% | 275 | 271 | 98% | 875 | 868 | 99% | 21 | 100% |
| February 1999 | 343 | 336 | 97% | 100 | 29 | 5 | 100% | 176 | 170 | 96% | 647 | 630 | 97% | 11 | 100% |
| March 1999 | 488 | 359 | 74% | 102 | 102 | 8 | 100% | 324 | 282 | 84% | 1073 | 884 | 82% | 108 | 100% |
| April 1999 | 430 | 367 | 85% | 64 | 46 | 7 | 100% | 259 | 221 | 85% | 945 | 831 | 88% | 94 | 100% |
| May 1999 | 366 | 285 | 78% | 81 | 109 | 2 | 100% | 239 | 200 | 84% | 875 | 729 | 83% | 140 | 100% |
| June 1999 | 364 | 269 | 74% | 80 | 105 | 7 | 100% | 262 | 204 | 77% | 837 | 655 | 78% | 86 | 100% |
| Summary (1998/99) | 4557 | 3915 | 86% | 1048 | 889 | 70 | 99% | 2879 | 2505 | 87% | 9832 | 8635 | 88% | 823 | 99% |
| July 1999 | 385 | 345 | 90% | 91 | 75 | 8 | 100% | 267 | 258 | 96% | 830 | 767 | 92% | 47 | 100% |
| August 1999 | 347 | 333 | 96% | 85 | 34 | 9 | 100% | 241 | 225 | 98% | 807 | 735 | 91% | 51 | 100% |
| September 1999 | 356 | 275 | 77% | 75 | 54 | 9 | 100% | 276 | 226 | 82% | 777 | 640 | 82% | 41 | 100% |
| Running Total for Current Year | 1088 | 953 | 88% | 251 | 163 | 26 | 100% | 784 | 709 | 90% | 2414 | 2142 | 89% | 139 | 100% |

Strategy and Asset Group

(August/September)

Strategy and Asset Group

Review of Operations

For the Period Ended 30 September 1999

1.	Items of Note

Sale of the Karori Reservoir site to the Karori Wildlife Sanctuary Trust is still held up due to negotiations between Wellington City Council and the Trust.  Meanwhile development of the land still owned by the Wellington Regional Council is proceeding at a pace.

A considerable amount of time has been spent during the period on Petone water supply issues.

Valuing The Water Group’s fixed assets, which is a major exercise, is proceeding.

The standby generator for the Te Marua Pumping Station was shipped from Australia during the period.  The project is on schedule.

Progress has been made with Hutt City Council on a pipeline easement through the Waiwhetu Tunnel.  There is a considerable difference between the easement value as determined by Hutt City Council’s advisors and the Wellington Regional Council’s advisors.  An arbitration type process is proposed as a way of resolving this.

A paper was presented at the Christchurch New Zealand Water and Waste Association by Murray Kennedy, with Jason Colton of Hyder Consulting as co-author.  It detailed the process trials at the Te Marua Water Treatment Plant and concluded that with direct filtration annual savings in the marginal cost of production will amount to about $300,000 a year.

- Sales Volume

Water Consumed from 1 April to 6 October 1999

A 1 percent overall decrease over the previous corresponding period, but with slight increases in consumption in Lower Hutt and Porirua Cities.  Percentage changes are represented below.

3.	Asset Management

- The initial asset data load into the Hansen AMS is complete and reports have been generated to facilitate the valuation exercise.  During October installation date data for the treatment plants (which has been collected) will be loaded into Hansen and reported, to enable completion of the revaluation.  The Hansen Valuation Module has been received and installed.  This module will provide a means of updating our asset value on a detailed basis annually.

- A review of the June 1998 Asset Management Plan has been commenced.  It is expected that this review will result in minor changes only, principally in the financial area.

- Local consultants Rolle Hillier Parker have been commissioned to carry out the revaluation of Wholesale Water assets, and work has begun.  They will consult with Engineering Consultancy Group staff on the valuation of pipeline assets.  The completion date for the commission is 30 October.

- Capital Works for 1999/2000 are underway.  Additional budget has been approved for the new switchboard at Gear Island and for the refurbishment of the OK main between Thorndon and Karori.  The Gear Island switchboard is to be installed during the latter part of October.  Tenders for the OK main refurbishment will be called in October.  A draft programme of capital works for 2000 to 2020 has been prepared.

- A consultant is preparing a resource consent application for a new well tapping the Moera Aquifer.  Consultation with IBM Ltd, whose fire fighting system could be affected by a new well, is proceeding, with slow progress being made.

- Draft Applications and Environmental Assessments for the new surface water take consents have been prepared, and forwarded to a range of groups and individuals for comment.  So far there has been little response.

- The consultant commissioned to build a control optimisation system for the Wainuiomata/Waterloo supply is making good progress.  Commissioning of Stage 1 (Wainuiomata/Waterloo system) is planned to commence on 25 October, and it is expected to be on line by mid December.  The optimisation system will manage source and pump use to minimise the cost of the production and distribution of water.

- Detailed seismic review work and risk assessment has been carried out for a number of network elements.  Report have been received on:

- Black Creek pipe crossing

- Gear Island Reservoir, buildings and structures

- Korokoro stream pipe crossings

- Haywards Reservoir

- The stream pipe crossing at the bottom of Haywards Hill

- Randwick Pumping Station

- Land slide potential at Haywards Reservoir site

- Potential for damage from landslides to the Orongorongo pipelines

- Potential for landslide damage to Kaitoke pipeline near the intersection of State Highways 2 and 58

These reports will be reviewed and summarised, and a programme of proposed strengthening or remedial works compiled.

- A proposal to build an hydraulic model to enable detailed study of the distribution network has been received.  However, this project will be put on hold until we have the Stage 1 optimiser in place, as the demand on staff time is high for both projects.

4.	Quality Assurance

- An ISO 9002 recertification audit was conducted by BVQI on 14/15 September.  A good report was received and our certification confirmed for another three years.

- Statistical analyses of turbidity readings to demonstrate compliance with the rule that requires turbidity to be less than 0.5 NTU for 95 percent of the time have been carried out.  The results for August and September are set out below.  The percentage of the time turbidity is less than 0.1 NTU has also been calculated.

| Percentage Compliance | Turbidity < 0.5 NTU |  | Turbidity < 0.1 NTU |  |  |
| --- | --- | --- | --- | --- | --- |
| Plant | August | September |  | August | September |
| Te Marua | 99.99% | 99.99% |  | 97.88% | 99.43% |
| Wainuiomata | 99.63% | 99.7% |  | 78.02% | 64.38% |

Software to analyse the data to check compliance with the rule requiring less than a 0.2 NTU rise in turbidity within ten minutes is being developed.  These two rules are intended to reduce the risk of Giardia and Cryptosporidium getting through the plant undetected.

- Work is continuing on the proposed Environmental Management System under ISO 14001.  A revised Environmental Policy, compressed to a single page, has been prepared.  Draft objectives and targets have been written and reviewed, and approved by the senior management team.

5.	Marketing and Economics

5.1	Market Research

A research project to investigate public attitudes towards the service provided by our Operations Network Section was advanced.  A quantitative research survey was designed in conjunction with C M Research and has now been completed.  The results are currently being used to design follow-up research.  This will investigate the reasons behind attitudes that have the greatest impact on the public’s overall perception of the Operations Network Section’s performance.  Details are outlined in a separate report.

5.2	Summer Water Conservation Campaign

Our territorial authority customers have been presented with a proposal for the 1999/2000 water conservation campaign and have given their approval for the strategy outlined, including the use of television advertising.  The detail of this proposal will now be confirmed.

5.3	1998/99 Business Report

Work continues on The Water Group’s 1998/99 Report of Business Activity.  A design has been confirmed and the text has been written and is close to final edit stage.  Photographs and other images have been arranged and the majority of financial information and annual statistics have been compiled for the second section of the report.  The report should be available for mailing by 30 November.

5.4	Public Relations

Issue 2 of the staff newsletter Water Group News was completed.

Discussions started with our Information Technology Department and Internet developers Clearview to have The Water Group’s monthly and annual quality information posted to the Regional Council’s Internet site.

5.5	Economics

- A new revenue meter database was installed to replace one that was not Y2K compliant.  Both systems will be run in parallel until the new system is proven.

- Work has started on gathering the data for the annual PriceWaterhouseCoopers’ run benchmarking survey.

- A draft electricity contract was sent to our legal advisors for checking.

6.	Projects undertaken by Engineering Consultancy for the Strategy and Asset Group

### Te Marua Lakes to Treatment Plant Pipeline

A design report has been prepared detailing the proposed method of rehabilitating the relaid bitumen lined pipes with cement mortar lining.

- Wainuiomata Reaction Tank

The reaction tank has been successfully commissioned by the Operations Group.  The Operations Group has been optimising the full treatment process, including the reaction tank.  The Engineer to the reaction tank construction contract has received the final claim from the Contractor.  The Engineer is processing this claim and assessing whether time extensions or liquidated damages are due.

- Orongorongo Pipeline : Intake to Tunnel

The fences and retaining walls have been finished off.  This project is now complete.

- Orongorongo Pipeline : Petone Esplanade

This pipeline has been successfully recommissioned to allow water from the Waterloo Water Treatment Plant to be supplied to the new Rahui Reservoir.

- Orongorongo Pipeline : Thorndon to Karori

Contract Documents for slip lining 300 m of this pipeline have been prepared.  This Contract is for the section through the Karori Road Tunnel between Waiapu Road and The Rigi.  The work is to be carried out in January 2000.

- Waterloo Capacity Increase

A minor problem was identified with the power supply to the variable speed drives.  This has been rectified by the Contractor.  A vibration problem on Pump No. 1 has also been rectified.

Pipework rearrangement at Randwick pump and valve chamber has been detailed.  The Distribution Section will be undertaking this work.

- Rahui Reservoir Rising Main

The telemetry and controls at the reservoir have been completed in preparation for commissioning this new reservoir.

###### Plimmerton/Pukerua Bay Branch Pipeline Shut-off Valve

Contract Documents are about to be completed for the installation of an emergency shut-off valve on this pipeline.

- Hutt Estuary Bridge Pipelines

A report has been prepared proposing fitting flexible couplings on the pipelines across Hutt Estuary Bridge.  The couplings are to allow for movement of the bridge in an earthquake.  It is proposed that the design of the couplings be not finalised until the bridge strengthening design work is completed by Hutt City Council.

###### Wainuiomata River Bridge

The Contract for removal of the old deck and strengthening of the abutments and central pier has started.

#### Karori Reservoir Rationalisation

Following the decommissioning of the open water storage at Karori significant alterations in pipework connections has been required to rationalise the pipework layout.

This was a major project and involved the removal of many large redundant valve and pipes.

The final stage of rerouting the rising mains to Kelburn and Messines Road is in progress.

- Haywards Reservoir Utilisation

New control valves and pipework are proposed for Haywards Reservoir.  This is to allow remote control, turnover in the reservoir to maintain water quality and greater utilisation of the available water storage.  A design report on the proposed work has been prepared.

- Water Meter Replacement Programme

The programme of replacing the existing revenue meters is progressing satisfactorily.  Fifteen meters have been replaced with high accuracy electromagnetic flow meters.  Design of the remaining installations is being carried out.  Quotations have been called, for the supply of the remaining meters to be installed this financial year.

Engineering Consultancy Group

(August/September)

Engineering Consultancy Group

Review of Operations

For the Period Ended 30 September 1999

1.	Work Carried Out for the Strategy and Asset Group

The main capital projects are itemised in the Strategy and Asset Group report.

Substantial progress has been made in scanning the substantial number of plans produced prior to CAD.  This will enhance plan security and access, as previously microfilms were the only back-up available.

2.	Work Carried Out for the Operations Group

The Engineering Consultancy Group has continued to provide support for smaller projects arising from the operation and maintenance of the wholesale water supply system.

3.	Work Carried Out for Wellington City Council

3.1	General

The Wellington City Council 1998/99 Capex jobs are nearing completion, with various difficulties having been overcome.  Commissions have now been received for some 1999/2000 main laying projects.

Current projects underway are detailed in the following sections.

  - Pipeline Projects

Contracts are underway for replacement mains in Owhiro Bay Parade, Helston Road and for various rider mains.  The inlet main in Makara Road to the new Karori South Reservoir has been completed.

Work has commenced on design of a replacement main in Fox Street, Ngaio.  Commissions have been received for two difficult inner city projects.  These are Manners Street, from Cuba to Willis Street, and Cuba Street, from Ghuznee to Webb Street.

An analysis has been carried out of the proposed conditions of contract and technical specifications prepared by Wellington City Council for use on these projects.

3.3	Wadestown Reservoir

Montgomery Watson Ltd has been engaged for the design of a replacement reservoir, capacity 1,800 cubic metres, along with the obtaining of resource consents necessary for work on the Town Belt.

The application for a notified resource consent has been lodged.  This included the AEE and design report.

3.4	Karori South Reservoir

This 800 m³ reservoir is complete and commissioned with the new rising main in Makara Road.

A proposal has been prepared to carry out the various interconnections to create the new larger zone and to allow the decommissioning of the Allington Road Pumping Station and removal of the associated precast concrete tanks.

  - Eastern Suburbs Storage

There is a storage deficit in the Low Level Zone of 10 ML.  This was identified and reported on at the time of approval of the Macalister Park 20 ML Reservoir.  Of this storage, approximately 7 ML is required in the Eastern Suburbs (Miramar) and 3 ML in the Southern Suburbs (Island Bay).

Because these reservoirs will balance on the Low Level Zone, a very careful analysis is required to establish the optimum reservoir levels.  Additional pressure monitoring points have been established at the Moa Point Sewage Treatment Plant and Kilbirnie Crescent.  Network modelling was undertaken to establish levels for the reservoir at different sites, as well as enhancement required to the pipe network.  The report has been forwarded to Wellington City Council.

3.6	Work Related to the Facilities Management Contract

Maintenance of the plan record system so that these are up-to-date, incorporating any alterations, has continued.  Continuing assistance has been given to Wellington City Council in the transfer of plan records into the City Council system.  Subdivisions are assessed for compliance with the Code of Practice and approval given.

Project Information Memoranda (PIMs) and Land Information Memoranda (LIMs) are processed on a regular basis for the City Council.

3.7	Asset Valuation

Significant additional valuation analysis of the water supply assets of Wellington City Council was carried out by updating earlier assessments.  In addition, input was provided to the Wellington City Council Asset Management Plan.

4.	Other Projects

4.1	River Surveys

Cross sectional surveys have been carried out on the Hutt River at Melling.

4.2	Pakuratahi Forest Access Road

The Contract for the continuation of the access road from this forest to State Highway 2, near the top of the Rimutaka Hill, is complete and in the maintenance period.  The work has been designed and was carried out so as to minimise visual and physical impacts.  Progress slowed because of harder rock conditions at the end of the job.  Logging trucks commenced using the road on Tuesday, 21 September 1999.

Laboratory Services

(August/September)

Laboratory Services Department

Review of Operations

For the Period Ended 30 September 1999

1.	Items of Note

The contract for sampling in Porirua was renewed and sampling continues as before.

Three demonstrations of information technology systems have been attended and a potential system identified.  The potential system appears to be highly flexible and reporting of results will be improved.  Results will be able to be accessed by some of our internal clients.

Small numbers of Giardia and Cryptosporidium were detected at Orongorongo, Wainuiomata River intake and Upper and Lower George Creek.

Giardia was identified at Kaitoke intake and Big Huia.

Summer sampling is to start on 1 November 1999.

2.	Financial

No financials are available at this point in time.

3.	Business Summary

3.1	Quality

There were no client requests for retesting samples.  Test reports are being sent out within the agreed time frames.

3.2	Health and Safety

There are no incidents to report.

3.3	Number of Samples Analysed

| August | September |
| --- | --- |
| Samples 942 Approximate tests 3,800 | Samples 896 Approximate tests 3,700 |

Plantation Forestry

(August)

Plantation Forestry Department

Review of Operations

For the Period Ended 31 August 1999

1.	Log Harvest Contract

The best month yet in August with 6,565 tonnes felled and a royalty of $179,800. The pruned crop produced an average royalty of $27.38/tonne.  Output by grade was:

| August 1999 |  |  |
| --- | --- | --- |
|  | Tonnes | Percentage |
| Pruned domestic | 1,027.1 | 15.6 |
| Pruned shorts | 421.5 | 6.4 |
| S Grade | 243.3 | 3.7 |
| A Grade | 324.1 | 4.9 |
| L Grade | 453.89 | 6.9 |
| R Grade | 557.9 | 8.5 |
| Pulp Domestic | 1,549.6 | 23.6 |
| Pruned Export | 0 | 0 |
| Sawlog Export | 51.2 | 0.8 |
| Rough Export | 1,812.7 | 27.6 |
| Pulp Export | 0 | 0 |
| Firewood | 124.8 | 1.9 |
| Total | 6,565.94 |  |

The recent wet weather has necessitated additional metalling and, while this has caused some damage to Hydro Road that runs between the logging site and the metal source, logging has continued at a good rate.  Additional culverts were installed to replace to fords as siltation was occurring from the trucks.

There have minor variations in price both up and down but nothing of significance.

2.	Silviculture Contracts

The 1998/99 silviculture contracts are substantially completed, with only some minor additional work that was outside the original contracts to be completed.

Replanting at Whakatikei has commenced and should be completed in early September.  The suitable weather allowed planting to continue later than planned and the additional area planted will gain one year’s growth, as well as staying ahead of the regenerating weeds and gorse.

Douglas Fir was planted on the margins of the incline and the opportunity was taken to replace any of last year’s plantings on the river flats that have succumbed to the wet winter.

3.	Plantation Forestry Operations

We have had to suspend the windrowing at Whakatikei because of the cost.  We are looking at options of either a lower standard of windrowing or deferring the work until summer to increase the machine productivity.  Unfortunately any decision to delay will give the weeds an opportunity to become established and may result in the need to release before planting.

The cost of releasing in Pakuratahi has been reduced from $550/ha to $415/ha. This, together with a review of the area to be treated, should bring the operation back close to budget.

The Cyclaneusma outbreak that was predicted by the MoF is starting with evidence of infestation in the Cook Blocks in Puketiro.  There is no treatment for this disease.

4.	Forest Access

Access has been maintained to all blocks.

The construction of the New Pakuratahi East Road is continuing to schedule, with completion anticipated around 18 September.  The same Contractor has been awarded the Contract to construct the connecting road to Kelly’s Track and to do the track upgrades and skid construction for the new harvest contract.

Hopefully all the “new” road construction required for Whakatikei has now been completed with only maintenance required until the completion of harvesting in mid-November.  The good soils produce large trees but do not result in good roads.

Discussions on an alternative route for logs from Puketiro are continuing.  This is proving to be a far more complicated process than first thought.  The fact that our road runs through a section of land with no title and therefore no owner has not assisted.

5.	Market Trends

Further improvements in prices are anticipated.  Rayonier has succeeded in achieving a permanent price increase of around $7/tonne for pulp and are seeking a further increase from later this year.

This change will be especially beneficial for pulp from Pakuratahi East, as the reduced cartage cost will result in a positive royalty for pulp for the first time in many years.