Water Supply

(January/February 2000)

Operations Group

(January/February 2000)

Operations Group

Review of Operations for the Period Ended 29 February 2000

1.	Items of Note

- No excessive supply demands were experienced during the period.  The peak recorded demand occurred on 20 January 2000 at a level of 197.3 ML per day.

- It is pleasing to note that the performance of the treatment plants is becoming more reliable, resulting in fewer call-outs because of plant malfunction.

- The period of high levels of rainfall at the beginning of February caused a slip to occur on the walking track from the access road to the Orongorongo intakes.  This will create access problems should the jigger be out of action and alternative access routes are being investigated.

2.	Water Quality

A total of 442 samples from trunk mains were tested for coliform organisms.  None of these samples tested positive.

Secchi disc water clarity in the Te Marua north lake varied between 4.7 m and 7.8 m, and in the south lake between 3.8 and 6.5 m.  These are considered satisfactory.  The dominant phytoplankton were as follows:

- North Lake:  Oscillatoria, Synedra, Asterionella

- South Lake:  Synedra, Staurastrum, and Peridinium

Oscillatoria is a filter clogging algae when present in high concentrations.

Synedra produces a musty smell and slick tongue sensation when abundant

Staurastrum produces a grassy smell when abundant.

Dissolved oxygen and pH readings are also satisfactory.

Giardia and Cryptosporidium results were as follows:

Te Marua

Lakes		)	No Giardia

)	No Cryptosporidium

Intake		)	No Giardia

)	No Cryptosporidium

Treated Water	)	No Giardia

)	No Cryptosporidium

Wainuiomata

Treated Water	)	No Giardia

)	No Cryptosporidium

Lower George Creek	)	No Giardia

)	Low Cryptosporidium

Big Huia Intake	)	Low Giardia

)	No Cryptosporidium

Intake		)	Low Giardia

)	Low Cryptosporidium

George Creek South arm	)	Low Giardia

)	Low Cryptosporidium

Orongorongo

Intake 		)	Low Giardia

)	Low Cryptosporidium

During January and February 2000 23 transgressions were notified:

- 9 low fluoride

- 2 high chlorine

- 2 high pH

- 1 low pH

- 1 presumptive coliform

- 2 high turbidity

- 2 high iron

- 4 high alkalinity

3.	Supply Situation

The two monthly seasonal forecast for February and March 2000 issued by the Meteorological Service is as follows:

Situation as at 10 February:

For Wellington:

Rain: 			Slightly below to about normal

Wind: 			Less than normal

Temperature: 	Above normal

Sunshine: 		Above average

Specials:		Stretches of dry weather lasting several days

Confidence: 		Moderate

After a notable cool start to summer with more southerly events than normal, the rest of the summer looks set to offer lighter winds and extended sunny periods.  There will still be a few cold fronts bringing some top-up rainfall but these should be spaced a week or more apart.

Hutt River Flows

The mean monthly river flow for the month of February was slightly below average

Wainuiomata River Flows

River flows in the Wainuiomata River for February were average.

Aquifer Levels

The aquifer level for February was above normal.

4.	Production

4.1	Wainuiomata

4.1.1	Quality

- Fluoride and polyelectrolyte supplier issues are being worked through.

- Both the treatment plant and washwater recovery plant polymer blenders have failed a couple of times during this period.  The trial flow meter to detect these failures was unsuccessful and we are now looking at other options.

- There have been a few periods of heavy rain where it was not feasible to run the treatment plant.

4.1.2	Safety

There are no accidents or incidents to report.

4.1.3	Operations

28 January:		The plant was off for 24 hours to comply with the discharge consent.

14 February:		The washwater settling tank was cleaned and the George Creek scour unblocked.

4.1.4	Plant Tours

24 February: 		Environmental students : 12 people

4.1.5	General

- A good size part of the walking track from the end of the Orongorongo road to the intakes slipped away mid-January.  This was repaired on 14 February.  Four days later heavy rainfall washed the track out again.  This track was built as a temporary track used for access during the Orongorongo Upgrade Project.  There are a few more areas along the track that are likely to slip into the river.

- In late January the jigger disk brake disc broke causing $4,500 worth of damage.  This took three weeks to repair.

- An old walking track known as the “steep track” was reinstated.  Even with the slip, the damaged track is more likely to comply with any health and safety standards than the steep track.  Some investigation work is required.

4.1.6	Projects

Capital Works

- The outlet flow meter is programmed to be replaced during the week beginning 10 April 2000

Operational Projects

- The new coagulant storage tanks and enclosed bund area is 95 percent complete.

- The washwater recovery plant standby pump modifications are nearing completion.

- Asset management labelling is 90 percent complete.

- The control philosophy for the PLC software modifications has been written.

4.2	Waterloo Water Treatment Plant

4.2.1	Quality

- Fluoride supplier issues are being worked through.

4.2.2	Safety

There are no accidents or incidents to report.

4.2.3	Operations

18 January:		The main switch for the Mahoe Street well pump caught fire, destroying part of the controls.  Three well pump control panels are to be refurbished before the end of this financial year.  This will limit Waterloo to a maximum flow rate of 103 MLD.

19 January:		The A stream reservoir had its six monthly clean and inspection.  The curtains inside the reservoir were also modified to cope with the higher flows.

10 February:		Vectron Industries Ltd modified all three Wellington variable speed drive power supplies.  Their investigations led them to think that this was the cause of the failures.

4.2.4	Plant Tours

There were no plant tours during the period.

4.2.5	General

There have been no variable speed drive failures since November.  Confidence in the drives is starting to return.

4.2.6	Projects

Capital Works

- The system optimisation project commissioning is to begin in March.

Operational Projects

- The Mahoe refurbished well pump has been returned.

4.3	Gear Island

4.3.1	Quality

There are no quality issues to report.

4.3.2	Safety

There are no accidents or incidents to report.

4.3.3	Plant Tours

There were no tours during the period.

4.3.5	General

- A new ceiling and roof has been put on the treatment building.  We are now looking forward to a dry winter.

4.3.6	Operational Projects

- Labelling of assets for the asset management system is complete

4.4	Te Marua

4.4.1	Quality

There are no quality transgressions to report.

4.4.2	Safety

While hosing down filters, an operator was stung by a bee.  No serious side effects were reported.

4.4.3	Operations

7 January:		A treated water high turbidity spike was caused by filter drain down.

12 January:		The thickener supernatant sump level sensor failed.  a new sensor was installed.

20 January:		There was a faulty level signal on the process water reservoir.  An intermittent cable fault was found.  Spare cores were connected.  Further investigation is underway (possible rodent damage).

17 February:		High treated water colour alarm was caused by a faulty instrument.

18 February:		A streaming current detector alarm was caused by a power surge tripping the pumping station boost pump.

22 February:		Plant slam shut was caused by a filter 6 high turbidity spike.

23 February:		Streaming current detector alarm was caused by a fault in the lime system.

4.4.4	Plant Tours

19 January:		Malvina Major Retirement Village : 15 people

31 January:		Upper Hutt Rotary Club : 40 people

8 February:		Lower Hutt Probus Club : 25 people

9 February:		Normandale School : 140 people

9 February:		Water Industry Training Organisation : 3 people

4.4.4	General

- The 600 mm backwash control valve has been replaced after leaks were detected in the valve casing.  A close inspection revealed several areas of erosion, most likely caused by cavitation.  Modifications to valve control are being investigated to prevent any recurrence.

- Work has begun on repairing damaged areas of the Kaitoke weir.  Te Marua operational staff are working closely with the Contractor to ensure minimal disruption to normal operations.

- The Kaitoke No. 1 Tunnel and pipeline were shut down and drained to allow an inspection by Engineering Consultancy Group staff.

- Washwater recovery pump repair.  The thickener supernatant return pump has been overhauled and fitted with a new stator.  The pump began to vibrate badly and when dismantled showed signs of excessive stator wear.

5.	Distribution

5.1	Electrical Section

5.1.1	General

- A pressure monitor has been installed in the Porirua main near Paremata No. 2 Reservoir in preparation for connecting an excess flow valve.

5.1.2	System Optimisation

- New level transmitters were installed at Macalister Park and Carmichael Reservoirs.  The level transmitters at Wainuiomata 1, Wainuiomata 2, Point Howard, Onslow and Ngaio were checked and calibrated.  Power pulses were connected to the telemetry at Kaiwharawhara and Randwick Pumping Stations.

5.1.3	Randwick Valve Chamber

- All electrical and instrumentation equipment associated with the Wellington pumps was removed from the chamber.

5.2	Pipeline Section

5.2.1	Randwick Rebuild

- Following the installation of new check valves and the removal of the Wellington pumps modifications occurred to the external pipework following which anchor blocks were poured.

5.2.2	Randwick Valve Chamber

- As part of the routine maintenance programme, sandblasting and painting of all pipework, walls and support beams was completed.

5.2.3	Haywards Optimisation

- Exploratory work commenced at Haywards No. 2 Reservoir.

5.2.4	1050 mm Pipeline

- An ongoing maintenance programme was carried out on the pipeline section between Ngauranga Valve Chamber and Thorndon Pumping Station.

5.2.5	Electromagnetic Flow Meters

New meters have been installed at the following locations:

- Moores Valley (Wainuiomata No. 2) Reservoir

- Messines Road Reservoir

- Whitby Reservoir

They have been connected to the telemetry system and commissioned.

6.	Health and Safety

Total Injury/Illness/Incident Record

Production

There was one incident involving an operator being stung by a bee.  There were no serious side effects.

Distribution

There was one lost time accident when a cutting wheel kicked back and cut an employee’s inner thigh, resulting in an absence of five days.

Network

One service person is off work because of an accident at home.

Operations Network

Review of Operations for the Period Ended 29 February 2000

1.	Items of Note

- During the period 12 burst mains occurred.  These were all attended to within 30 minutes and all repaired within eight hours.

- The transition period through to 1 January 2000 passed without a hitch and there were no undue demands on the water reticulation within Wellington City.  The work involved the preparation for this event will be beneficial should any future emergency occur within the city boundaries.

- The introduction of the job despatch system has continued to produce excellent results, not only with the reduction in paperwork but improvement in the ability to produce reports on all work activities.

- We continue to review the operation of the section in order to achieve an efficient and cost effective service, and have appointed a person in the position of Out of Hours Supervisor to improve our response to out of hours calls.

- The number of jobs increased during February by 10 percent over the previous months.

2.	Water Supply (PT 30.1)

3.	Financial

Contract Amounts : Wellington, including Tawa

| Month | Actual $ | Budget $ | Variance % | Year to Date | Budget $ | Variance % |
| --- | --- | --- | --- | --- | --- | --- |
| January | 229,163 | 294,314 | -22.14% | 1,617,970 | 2,060,198 | -21.46% |
| February | 214,721 | 294,314 | -27.04% | 1,832,691 | 2,354,512 | -22.16% |

4.	Water Quality

Routine Testing (PT 1.1)

The water quality was monitored and the appropriate laboratory tests were completed for the months of January and February.  There were 170 samples from the reticulation system tested for bacteriological compliance in January and 152 in February.

Compliance for both months is 100 percent.  Compliance for the year to date is 100 percent.

Water Tests Initiated by Customers (PT 2)

|  |  | January | February | Year to Date | Compliance (%) Year to Date |
| --- | --- | --- | --- | --- | --- |
|  | Number received | 3 | 9 | 64 | - |
| (PT 2.2) | Within ability of Operations Network to control | 3 | 3 |  | - |
| (PT 2.1) | Formal response within five days | 3 | 7 | 61 | 95% |

5.	Customer Services

5.1	Counter and Other Office Services (PT 3.1), (PT 4.1), (PT 5.1)

|  |  | January | February |
| --- | --- | --- | --- |
|  | Counter enquiries | 53 +4 encroachments | 62 + 12 encroachments |
|  | Proposals from other utilities | 12 | 6 |
| (PT 33.1) | Plan records : New services recorded | 21 | 17 |
|  | Response time requirement compliance | 100% | 100% |

5.2	Complaints Register (Monthly Summary) (PT 5.1)

An enquiry/complaints register is being maintained.  A breakdown of complaints and enquiries received during the reporting period is as follows:

|  | Complaints |  |  |
| --- | --- | --- | --- |
|  |  | January | February |
| (PT 2.2) | Water quality | 5 | 12 |
| (PT 16.1.2) | Pressure | 1 | 6 |
| (PT 20.1) | Reinstatement | 0 | 0 |
| (PT 16.1.4) | No-water | 8 | 7 |
|  | Contractors | 0 | 0 |
|  | Other | 1 | 4 |

During January all of the “Water Quality” and “Pressure” complaints were responded to and completed within the performance criteria.  Three of the four “No-water” complaints were responded to and completed within the performance criteria.  The one job that failed was attended to one minute outside the 30 minute specification.  In February all of the “No-water” and “Pressure” complaints were responded to and completed within the performance criteria.  Seven of the nine “Water Quality” complaints were attended to in compliance with the performance levels.  Unfortunately two samples were taken in contaminated sample bottles.  These were to be retested in March.

6.	Response Maintenance

6.1	Compliance (PTs 9.1, 9.1a, 9.2, 10.1, 16.1)

|  |  | January |  |  | February |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | No. of Calls | Completed to Standard | Compliance % | No. of Calls | Completed to Standard | Compliance % |
| (PT 9.1) | Stopcocks | 391 | 341 | 87 | 467 | 389 | 83 |
| (PT 9.1) | Hydrants | 94 | 77 | 82 | 117 | 102 | 87 |
| (PT 9.1a) | Valves | 26 | 18 | 69 | 25 | 19 | 76 |
| (PT 9.2) | Other leaks | 237 | 182 | 77 | 222 | 196 | 88 |
| (PT 10.1) | Mark-outs | 40 | 40 | 100 | 57 | 57 | 100 |
| (PT9.1a) | Value repacks | 11 | 9 | 82 | 7 | 7 | 100 |
| (PT 16.1.1) | Burst mains | 7 | 7 | 100 | 5 | 6 | 100 |
| (PT 2.1) | Water quality complaints | 3 | 3 | 100 | 9 | 7 | 78 |
|  |  | 809 | 677 | 84 | 909 | 783 | 86 |

The results for January have been achieved with approximately 30 percent of the staff still absent on leave up until 17 January.

In compliance with the Business Continuity Plan for the new millennium all rostered staff members were on duty on New Year’s Eve.  The final report to the Wellington City Council was at 9 am on 5 January.

Failures

|  | Jobs Failed by 1-24 Hours |  | Jobs Failed by 1-5 Working Days |  | Jobs Failed >5 Working Days |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | January | February | January | February | January | February |
| Fire hydrants | 1 | 5 | 12 | 6 | 4 | 4 |
| Mains | 1 | 0 | 3 | 0 | 0 | 0 |
| Valve repacks | 0 | 0 | 2 | 0 | 0 | 0 |
| Valves | 3 | 0 | 1 | 6 | 4 | 0 |
| Services | 10 | 6 | 31 | 10 | 10 | 10 |
| Tobies | 16 | 19 | 27 | 36 | 7 | 23 |
| Total | 31 | 30 | 76 | 58 | 25 | 37 |

Additional Work Carried Out

|  | January | February |
| --- | --- | --- |
| New services | 11 | 13 |
| Damages by contractors | 16 | 58 |
| Variations | 6 | 16 |
| Renewals over 4 m | - | 4 |

6.2	Burst Mains (PT 16.1)

There were seven burst mains during the month of January and five burst mains in February.  They were as follows:

83 Taylor Terrace	4 January 2000

17 Raroa Terrace, Tawa	17 January 2000

Cnr Oriental Parade and Oriental Terrace	22 January 2000

Cnr Taranaki and Abel Smith Streets	25 January 2000

2 Shropshire Avenue, Wilton	26 January 2000

85 The Terrace, Lambton	28 January 2000

14 Warrington Grove, Newlands	31 January 2000

5 Shropshire Street	2 February 2000

4 Turriff Crescent, Tawa	7 February 2000

Cnr Taranaki and Buckle Streets	8 February 2000

18-21 Churchill Drive, Wilton	10 February 2000

Cnr Black Rock and Glanmire Roads	23 February 2000

All of the burst mains were attended to within 30 minutes and repaired within eight hours.

6.3	Supply (PT 16.1)

|  | January | February |
| --- | --- | --- |
| Total calls received regarding loss of or temporary loss of supply because of broken mains or supply failure | 4 | 2 |
| Total calls attended within 30 minutes | 3 | 2 |
| Total Compliance | 75% | 100% |

6.4	Reinstatement (PT 20.1)

There were no complaints received in either January or February.  The Facilities Management Contract target is less than 12.

6.5	Shutdown Notification (PT 6.1)

There were no planned shutdowns in January.  In February there were six planned shutdowns.  All identifiable customers received notification within 24 hours prior to the shutdown.

6.6	Locates and Investigations (PT 10.1)

Work completed during the two month period comprised:

|  | January | February |
| --- | --- | --- |
| Locate stopcocks | 83 | 135 |
| Leak location | 122 | 157 |
| Flow tests | 2 | 1 |
| Seepage/Investigations | 3 | 15 |
| Miscellaneous supply jobs | 15 | 14 |

7.	Health and Safety

There were no incidents to report in either January or February.

8.	Meters (PT 13.1)

A total of 1,493 suburb and high use meters were read and entered into the system by 23 January 2000.  An additional 974 voluntary meters were also read in January.  By 23 February 2000 a total of 1,395 city and high use meters were read and entered into the system.

9.	Pumping Stations, Reservoirs and System Control

9.1	General

Normal routine maintenance has resulted in the Wellington City system operating satisfactorily.

9.2	Control System (PT 30.1)

The new Realflex 4 Scada system was commissioned to replace the non-compliant older system at Mabey Road and The Regional Council Centre.  New Year’s Y2K event passed without incident.

The control system continues to operate satisfactorily.  The reservoir outlet magnetic flow meters that were installed by a Wellington City Council contractor have been connected to the telemetry system.  The sites are:

- Bell Road Reservoir outflow

- Broadmeadows Reservoir inlet/outlet flow

- Maupuia Reservoir outflow

- Maldive Regional Reservoir outflow

9.3	Johnsonville Pumping Station

The No. 1 pump motor burnt out and is beyond repair.  The small piping associated with the pump control valves has been replaced.

9.4	Chester Road Reservoir

A new pressure bulb was installed to improve the level measuring system.

9.5	Messines Road Reservoir

A new magnetic flow meter has been installed at the Messines Road Reservoir.

The old meter at Karori Pumping station has been disconnected.

9.6	Maintenance Checks (PT 17.4)

Maintenance has been carried out as follows:

| January | February |
| --- | --- |
| Round E | Round C |
| Johnsonville Pumping Station Ngauranga Reservoir/Pumping Station Kaiwharawhara Pumping Station Thorndon Pumping Station Karori Reservoir/Pumping Station Macalister Park Reservoir Churton Park CV Maldive Reg./Abb. CV Tawa Linden | Allington Road Messines Road Pumping Station Karori Park Montgomery Avenue Makara Road Verviers Street The Zoo Russell Terrace Lyndhurst/Chester Roads Mills Road Woodridge CV |
| Round F | Round D |
| Randwick Pumping Station Tunnel Grove Chamber Rocky Point Chamber Korokoro Valve Chamber Wainuiomata Pumping Station Moores Valley Pumping Station Mabey Road Generator Naenae Reservoir Gracefield Reservoir Rahui Reservoir | Karepa Street Highbury Landfill Reservoir Landfill CV Rhine Street Beacon/Signal Hill Townsend Road Miramar North Dargle Way Grenada CV Rangoon Heights Ngaio CV |

10.	Development

10.1	Development Statistics

| Subdivisions | January | February | Year to Date |
| --- | --- | --- | --- |
| Construction plans approved (lots/units) | 4 | 27 | 161 |
| Scheme plans approved | 24 | 26 | 233 |
| Subdivisions cleared (lots/units) | 63 | 67 | 382 |

10.2	Development Projects

10.2.1	Woodridge Reservoir

Hydroseeding, channel and minor details are now complete.  The reservoir has been fully taken over from the subdivider.  The reservoir is operating satisfactorily.  This project is now complete.

10.2.2	Churton North Reservoir

The reservoir is largely complete.  The TDI hut, control system and power are yet to be installed.  Completion is expected to coincide with completion of the Westchester Drive Pumping Station, at about the end of March 2000.

10.2.3	Westchester Drive Pumping Station

Final approval of the plans has been granted, with appropriate conditions.  Construction has commenced.  Pumps have been installed.  Walls have been built.  Completion is expected about the end of March 2000.

10.2.4	Major Subdivisions

Construction plans were submitted for approval of the following major subdivisions:

- 33 Parkvale Road, Karori (5 lots).  Approved on 18 February 2000.

- Downing Street Extension, Chartwell (15 lots).  Further information has been requested from the subdivider has not been finally approved as yet.

- 8 Atamira Close, Churton Park (7 lots). Further information has been requested from the subdivider has not been finally approved as yet.

- 29-37 Madras Street, Khandallah (9 lots).  Approved on 22 February 2000.

- Lots 5, 6 and 31 Waverton Terrace, Churton North (3 lots).  Approved on 17 February 2000.

- Lots 128-130 Amesbury Drive, Churton North (3 lots).  Approved on 28 February 2000.

- Marjory Close/John Sims Drive (6 lots).  Approved on 28 February 2000.

- 5 Hawtrey Terrace, Johnsonville (6 lots).  Further information has been requested from the subdivider has not been finally approved as yet.

- Woodridge, Stage 7 (31 lots).  This is under consideration and has yet to be finally approved.

- De Bes Subdivision, Beacon Hill (5 lots).  This is under consideration and has yet to be finally approved.

- Bellevue, Newlands : Black Rock Road (17 lots).  This is not yet finally approved.  We are waiting for approval from Wellington City Council.

As-built plans were submitted for approval of the following major subdivisions:

- 282 Takapu Road, Grenada North (7 lots).  Cleared on 20 January 2000.

- 6 Atamira Close, Churton Park (3 lots).  Cleared on 20 January 2000 .

- Greenvue, Stage 9 (Woodman Drive, Tawa) (22 lots).  This is not yet finally approved.  It is under consideration.

- Bellevue, Stages 6 and 7 (72 lots). This is not yet finally approved.  It is under consideration.

10.2.5	Fire Services Recently Connected (PT 12.1)

25-27 Vivian Street (100 mm diameter)

10.3	Building Development Appraisals

|  | January |  | February |  |
| --- | --- | --- | --- | --- |
|  | Commercial | Domestic | Commercial | Domestic |
| Building consents | 1 | 22 | 5 | 34 |
| PIMS applications | 1 | 20 | 5 | 34 |
| Compliance with response time requirement | 100% | 100% | 100% | 100% |

10.4	Land Information Memoranda

|  | January | February |
| --- | --- | --- |
| Applications processed | 21 | 47 |
| Compliance with response time requirement | 100% | 100% |

11.	Capital Works

11.1	Main Laying City

11.1.1	Taranaki Street

Ductile iron pipe for the replacement of the 150 mm cast iron main in Taranaki Street has been received and is stored at the Raroa Road pipe stack area. Wellington City Council is preparing the brief for the replacement of the 150 mm cast iron main in Taranaki Street.

11.1.2	Manners Street

The Contract to replace the 300 mm cast iron main from Willis to Cuba Street was awarded to C M Contracting Ltd.  The pipeline has been installed and final connections are being made.  This has been a particularly difficult job in a highly visible area.

11.1.4	Cuba Street

The Contract to replace the 100 mm and 200 mm cast iron mains from Ghuznee to Webb Streets is nearing completion.

11.2	Main Laying Suburbs

11.2.1	Contracts in Maintenance Period

The following pipelaying contracts are in the maintenance period.

- Tirangi Road, McGregor, Kingsford Smith and George Bolt Streets

- Bracken Road

- Breaker Bay Road

- Makara Road Rising Main

- Owhiro Bay Parade

- Helston Road

- Rider Main Renewals

- Fox Street

The maintenance period for the Johnsonville Road Contract has expired.  Arrangements are being made to rectify minor maintenance issues and to release the maintenance retentions.

11.2.2	Bell Road Zone Improvements

Drawings and Contract Documents for the replacement of pipes in Bidwill Street, Rolleston Street, Salisbury Terrace and Salisbury Avenue have been prepared and forwarded to Wellington City Council for approval.

11.3	High Level Distribution and Storage

11.3.1	Karori South Reservoir

The Karori South Reservoir construction contract is in maintenance.

The options to supply the Allington Road Zone from the new reservoir are being reviewed.

11.3.2	Wadestown Reservoir

The consultant has been instructed to proceed with the design and preparation of Contract Documents complying with the resource consent.

11.3.3	Grenada North High Level Reservoir

A design report has been approved by Wellington City Council for the proposed Grenada North High Level Reservoir.  The consultant has been instructed to proceed with the detailed design and resource consent application.

11.4	Low Level Zone Storage

11.4.1	Eastern Suburbs Storage Enhancement

Further investigations are underway in preparation for an Environmental Impact Assessment for the three potential sites.

| Analysis - December 1998 to February 2000 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Quality Reports PT 2.1 |  |  |  |  | No of Planned Shut-downs PT 6.1 |  |  | Stopcocks PT 9.1 |  |  |  |  | Leaking Hydrants PT 9.1 |  |  |  | Leaking Valves PT 9.1a |  |  | Leaks PT 9.2 |  |  |  |  | Mark-outs PT 10.1 |  |
|  | Calls Received | 5 Day Response |  | % Compl. |  | Completed |  |  | Calls Received | Completed |  | % Compl. |  |  |  |  | % Compl. |  | % Compl. |  | Calls Received |  | Completed |  | % Compl. | Received | % Compl. |
| July 1998 | 8 | 8/8 |  | 100% |  | 2 |  |  | 371 | 359 |  | 96% |  |  | 90 |  | 94% | 24 | 100% |  | 231 |  | 213 |  | 95% | 61 | 95% |
| August 1998 | 10 | 17/18 |  | 94% |  | 2 |  |  | 304 | 243 |  | 87% |  |  | 91 |  | 86% | 25 | 100% |  | 216 |  | 183 |  | 85% | 74 | 100% |
| September 1998 | 11 | 26/29 |  | 90% |  | 4 |  |  | 289 | 211 |  | 81% |  |  | 71 |  | 77% | 13 | 100% |  | 219 |  | 183 |  | 84% | 74 | 100% |
| October 1998 | 6 | 32/35 |  | 91% |  | 3 |  |  | 385 | 293 |  | 73% |  |  | 107 |  | 73% | 6 | 100% |  | 216 |  | 147 |  | 68% | 67 | 100% |
| November 1998 | 7 | 37/42 |  | 88% |  | 3 |  |  | 421 | 382 |  | 76% |  |  | 70 |  | 75% | 13 | 100% |  | 228 |  | 198 |  | 86% | 91 | 100% |
| # December 1998 | 9 | 46/51 |  | 92% |  | 2 |  |  | 365 | 362 |  | 90% |  |  | 79 |  | 78% | 9 | 100% |  | 234 |  | 233 |  | 99% | 16 | 100% |
| January 1999 | 13 | 59/64 |  | 93% |  | 25 |  |  | 431 | 429 |  | 99% |  |  | 77 |  | 64% | 15 | 93% |  | 275 |  | 271 |  | 98% | 21 | 100% |
| February 1999 | 10 | 69/74 |  | 93% |  | 30 |  |  | 343 | 336 |  | 97% |  |  | 106 |  | 81% | 18 | 94% |  | 176 |  | 170 |  | 96% | 11 | 100% |
| March 1999 | 5 | 74/79 |  | 94% |  | 34 |  |  | 488 | 359 |  | 74% |  |  | 118 |  | 94% | 12 | 92% |  | 324 |  | 282 |  | 84% | 108 | 100% |
| April 1999 | 5 | 79/84 |  | 94% |  | 18 |  |  | 430 | 367 |  | 85% |  |  | 129 |  | 91% | 20 | 95% |  | 259 |  | 221 |  | 85% | 94 | 100% |
| May 1999 | 8 | 86/92 |  | 93% |  | 18 |  |  | 366 | 285 |  | 78% |  |  | 110 |  | 78% | 10 | 80% |  | 239 |  | 200 |  | 84% | 140 | 100% |
| June 1999 | 5 | 90/97 |  | 93% |  | 18 |  |  | 364 | 269 |  | 74% |  |  | 90 |  | 68% | 21 | 95% |  | 262 |  | 204 |  | 77% | 86 | 100% |
| Summary (1998/9) | 97 | 90/97 |  | 93% |  | 159 |  |  | 4557 | 3915 |  | 86% |  |  | 1138 |  | 81% | 186 | 96% |  | 2879 |  | 2505 |  | 87% | 823 | 99% |
| July 1999 | 16 | 15/16 |  | 94% |  | 18 |  |  | 385 | 345 |  | 92% |  |  | 72/78 |  | 92% | 18/19 | 95% |  | 267 |  | 258 |  | 96% | 47 | 100% |
| August 1999 | 6 | 6/6 |  | 100% |  | 15 |  |  | 347 | 333 |  | 91% |  |  | 85/89 |  | 96% | 16/19 | 84% |  | 241 |  | 225 |  | 98% | 51 | 100% |
| September 1999 | 1 | 1/1 |  | 100% |  | 12 |  |  | 356 | 275 |  | 82% |  |  | 68/72 |  | 94% | 18/20 | 90% |  | 276 |  | 226 |  | 82% | 41 | 100% |
| October 1999 | 13 | 13/13 |  | 100% |  | 21 |  |  | 320 | 241 |  | 75% |  |  | 71/87 |  | 81% | 19/20 | 95% |  | 234 |  | 198 |  | 85% | 40 | 100% |
| November 1999 | 12 | 12/12 |  | 100% |  | 16 |  |  | 365 | 334 |  | 92% |  |  | 81/92 |  | 88% | 11/13 | 85% |  | 246 |  | 228 |  | 93% | 30 | 100% |
| December 1999 | 4 | 4/4 |  | 100% |  | 8 |  |  | 364 | 346 |  | 95% |  |  | 77/80 |  | 96% | 21/32 | 66% |  | 218 |  | 194 |  | 89% | 28 | 100% |
| January 2000 | 3 | 3/3 |  | 100% |  | 0 |  |  | 391 | 341 |  | 87% |  |  | 77/94 |  | 82% | 18/26 | 69% |  | 237 |  | 182 |  | 77% | 40 | 100% |
| February 2000 | 9 | 7/9 |  | 78% |  | 6 |  |  | 467 | 389 |  | 83% |  |  | 102/117 |  | 87% | 19/25 | 76% |  | 222 |  | 196 |  | 88% | 57 | 100% |
| Running Total for Current Year | 64 | 61/64 |  | 95% |  | 96 |  |  | 2,995 | 2,604 |  | 87% |  |  | 633/719 |  | 88% | 140/174 | 81% |  | 1,941 |  | 1,707 |  | 88% | 334 | 100% |
| Analysis - December 1998 to February 2000 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ## Loss of Supply ## PT 16.1 |  |  |  | Burst Mains PT 16.11 |  |  | Reinstatements PT 20.1 |  |  |  |  | Toby Locates |  |  | Damage Repairs |  | Total Calls |  |  |  |  |  |  |  |  |  |
|  | Complaints Received |  | % Compl. |  | Occurred |  | % Compl. | Occurred |  |  | % Compl. |  |  |  |  |  |  | Calls Received |  | Completed |  | % Compl. |  |  |  |  |  |
| July 1998 | 29 |  | 97% |  | 6 |  | 100% | 3 |  |  | 100% |  | 81 |  |  | 91 |  | 791 |  | 753 |  | 95% |  |  |  |  |  |
| August 1998 | 31 |  | 97% |  | 2 |  | 100% | 4 |  |  | 100% |  | 89 |  |  | 100 |  | 703 |  | 613 |  | 81% |  |  |  |  |  |
| September 1998 | 30 |  | 100% |  | 8 |  | 100% | 1 |  |  | 100% |  | 97 |  |  | 98 |  | 683 |  | 553 |  | 81% |  |  |  |  |  |
| October 1998 | 29 |  | 83% |  | 5 |  | 100% | 0 |  |  | 100% |  | 72 |  |  | 57 |  | 795 |  | 605 |  | 76% |  |  |  |  |  |
| November 1998 | 24 |  | 96% |  | 9 |  | 90% | 3 |  |  | 100% |  | 89 |  |  | 103 |  | 838 |  | 751 |  | 90% |  |  |  |  |  |
| # December 1998 | 15 |  | 80% |  | 4 |  | 100% | 1 |  |  | 100% |  | 101 |  |  | 26 |  | 770 |  | 763 |  | 99% |  |  |  |  |  |
| January 1999 | 21 |  | 100% |  | 7 |  | 100% | 1 |  |  | 100% |  | 92 |  |  | 23 |  | 875 |  | 868 |  | 99% |  |  |  |  |  |
| February 1999 | 25 |  | 96% |  | 5 |  | 100% | 0 |  |  | 100% |  | 100 |  |  | 29 |  | 647 |  | 630 |  | 97% |  |  |  |  |  |
| March 1999 | 32 |  | 97% |  | 8 |  | 100% | 0 |  |  | 100% |  | 102 |  |  | 102 |  | 1073 |  | 884 |  | 82% |  |  |  |  |  |
| April 1999 | 46 |  | 94% |  | 7 |  | 100% | 1 |  |  | 100% |  | 64 |  |  | 46 |  | 945 |  | 831 |  | 88% |  |  |  |  |  |
| May 1999 | 32 |  | 100% |  | 2 |  | 100% | 1 |  |  | 100% |  | 81 |  |  | 109 |  | 875 |  | 729 |  | 83% |  |  |  |  |  |
| June 1999 | 33 |  | 85% |  | 7 |  | 100% | 3 |  |  | 100% |  | 80 |  |  | 105 |  | 837 |  | 655 |  | 78% |  |  |  |  |  |
| Summary (1998/9) | 347 |  | 94% |  | 70 |  | 99% | 18 |  |  | 100% |  | 1048 |  |  | 889 |  | 9832 |  | 8635 |  | 88% |  |  |  |  |  |
| July1999 | 19/22 |  | 86% |  | 8 |  | 100% | 4 |  |  | 100% |  | 91 |  |  | 75 |  | 830 |  | 767 |  | 92% |  |  |  |  |  |
| August 1999 | 14/16 |  | 88% |  | 9 |  | 100% | 0 |  |  | 100% |  | 85 |  |  | 34 |  | 807 |  | 735 |  | 91% |  |  |  |  |  |
| September 1999 | 50/50 |  | 100% |  | 9 |  | 100% | 1 |  |  | 100% |  | 75 |  |  | 54 |  | 777 |  | 640 |  | 82% |  |  |  |  |  |
| October 1999 | 17/17 |  | 100% |  | 4 |  | 75% | 0 |  |  | 100% |  | 76 |  |  | 22 |  | 724 |  | 591 |  | 82% |  |  |  |  |  |
| November 1999 | 9/10 |  | 90% |  | 8 |  | 100% | 1 |  |  | 100% |  | 72 |  |  | 29 |  | 774 |  | 709 |  | 92% |  |  |  |  |  |
| December 1999 | 23/23 |  | 100% |  | 5 |  | 100% | 1 |  |  | 100% |  | 64 |  |  | 20 |  | 744 |  | 681 |  | 92% |  |  |  |  |  |
| January 2000 | 3/4 |  | 75% |  | 7 |  | 100% | 0 |  |  | 100% |  | 83 |  |  | 16 |  | 809 |  | 677 |  | 84% |  |  |  |  |  |
| February 2000 | 2/2 |  | 100% |  | 5 |  | 100% | 0 |  |  | 100% |  | 135 |  |  | 58 |  | 909 |  | 783 |  | 87% |  |  |  |  |  |
| Running Total for Current Year | 137/143 |  | 96% |  | 55 |  | 98% | 7 |  |  | 100% |  | 681 |  |  | 308 |  | 6,374 |  | 5,583 |  | 88% |  |  |  |  |  |

Strategy and Asset Group

(January/February 2000)

Strategy and Asset Group

Review of Operations for the Period Ended 29 February 2000

1.	Items of Note

- The first stage of upgrading the pipeline from Thorndon to the Karori Pumping Station has been completed.  This will improve the reliability of supply to Karori, Kelburn and the Aro Valley.

- The Landcare Division organised a ballot for recreational shooters to cull deer in the Wainuiomata and Orongorongo Catchments for a four week period in April.  This is part of the animal control programme.

- Hutt City Council signed an agreement in December 1999 to allow use of the upper tunnel through the Wainuiomata Hill for a sewerage pipe.  They are now investigating the possible use of the lower tunnel.

- A report on public perception of water quality will be available for the next meeting of the Utility Services Committee.

- Hutt City Council has advised us of some problems with iron levels in the Petone water supply.  The testing frequency for iron at the new Rahui Reservoir has increased to weekly.  The issue is still being discussed with the Hutt City Council.

- Sales Volume : Water Consumed from 1 April to 22 March 2000

- A 2.7 percent overall decrease for the year to date over the previous corresponding period last year.  This appears to result from less garden watering.  Rainfall was more frequent in December and January.

- Percentage changes are represented above.

Note:		The above charts are for the period ending 22 March 2000 as the system had been updated.

3.	Asset Management

- The Revaluation of Wholesale Water Assets has been completed.  A detailed reconciliation exercise is underway to ensure that the assets valued are consistent with those we actually own and use as recorded in the Hansen Asset Management System.

- A review of the June 1998 Asset Management Plan has commenced.  It is expected that this review will result in minor changes only, principally in the financial area.

- Capital works for 1999/00 are progressing.  The slip lining of the OK main in Glenmore Street has been completed and a start will be made on relining wholesale water mains at Te Marua in early March.  Commissioning of Stage 1 of the System Optimiser is now scheduled for 27 March.  The System Optimiser will select water sources and manage pump use to minimise the cost of the production and distribution of water.

- A resource consent application for a new well tapping the Moera aquifer at Gear Island is being prepared.  A new well may affect IBM’s firefighting wells.  To check this, tests on the IBM well are to be undertaken.  An investigation bore being drilled into the Moera aquifer near Ewen Bridge by the Consents Investigations Department has shown limited water flows to date.

- Applications and environmental assessments for new surface water take consents have been prepared.  Following a review of the operational impacts of the proposed new consent regime, some changes to the application for the Orongorongo Catchment are to be made.  A report will be prepared for the next Utility Services Committee meeting.

- An application for a resource consent to discharge supernatant into the Wainuiomata River intermittently has been lodged.  Concurrently a proposal has been put to Hutt Valley Health to enable most supernatant to be recycled back through the treatment plant.  Hutt Valley Health has requested that a water quality risk management plan be prepared before they will sanction this request.

- Detailed seismic review and risk assessment work has been carried out for a number of network elements.  These reports have been reviewed and summarised, and a programme of proposed strengthening and remedial works compiled.

- Work has begun on the compilation of a risk policy, which will provide broad guidelines for the management of risks to the water business.

3.	Quality Assurance

- Statistical analyses of turbidity readings to demonstrate compliance with the rule that requires turbidity to be less than 0.5 NTU for 95 percent of the time have been carried out.  The results for January and February are set out below.  The percentage of the time turbidity is less than 0.1 NTU has also been calculated.

| Percentage Compliance | Turbidity <0.5 NTU | Turbidity <0.1 NTU | Turbidity <0.5 NTU | Turbidity <0.1 NTU |
| --- | --- | --- | --- | --- |
| Plant | January | February | January | February |
| Te Marua | TBA | TBA | TBA | TBA |
| Wainuiomata | 99.52 | 99.87 | 87.19 | 95.28 |

This rule is intended to reduce the risk of Giardia and Cryptosporidium passing through the plant.  The plants incorporate “slam shut” valves so that any water that does not comply with the 0.5 NTU rule is not delivered to the customers.

- A computer program called Q-Pulse has been installed and is being used to manage the documentation for the Quality and Environmental Management Systems.   It is accessible at all Water Group sites, providing direct on-line access to the latest version of procedures and manuals.  It will also be used to mange the internal audit process and the processing of Improvement Opportunity Forms, which are generated when a non-compliance is identified.

- Work is continuing on the proposed Environmental Management System being developed under the provisions of ISO 14001.  Procedures have been developed and put in place, internal audit training completed and a number of internal audits completed.  The initial document review certification audit is scheduled for 21 March.  This will be followed by a full certification audit a few weeks later.

5.	Marketing

5.1	Summer Water Conservation Campaign

- Screening of a television commercial, featuring Maggie Barry promoting water efficient gardening and watering techniques, commenced on 9 January and ran for a duration of six weeks.  The commercial screened on Television New Zealand (TVNZ) channels only.  Television One is the dominant channel in Wellington overall and is particularly strong with older viewers, our main target audience.  Using only TVNZ entitled us to a substantial discount on normal rate card charges.  The campaign was designed to achieve ratings of 250 “target audience rating points” (TARPs) in the first week of screening and 200 per week for the remaining five weeks with an audience of “all people aged 30+”.  It actually achieved 395 TARPs in week one and an average of 243 in weeks 2-5.  Ratings against “women aged 40+” (who are most likely to be garden water users) were even better.  Post-campaign research will provide information about recall of the advertisement. This will be available in early April.

- A press release regarding Maggie Barry’s involvement in the Summer Water Conservation Campaign was issued on 7 January.  The story was also covered in Coast to Coast and Elements.

- Sunshine hours and rainfall were monitored on a daily basis as a predictor of demand for water.  A Weekly Water Watch bulletin was issued to customers and Councillors to keep them informed of the summer water supply situation.

5.2	Public Relations

- Arrangements were made for eight visits to treatment plants and five other requests for information were responded to.

5.3	Other Activities

- The Utility Services and Environment Divisions are working together to ensure that Environment’s Learnwell programme being developed for water conservation will address Utility Services’ objectives for educational material, as well as Environment’s.  A briefing paper about the aims and outcomes The Water Group is seeking from its involvement with Learnwell was written and presented to the Environment Division. Development of objectives is continuing.

- A paper was researched and written appraising the value of producing promotional bottles of water.  This idea was raised as a possible strategy to counter the attacks on potable water quality made or implied by water filter and still manufacturers.  A comprehensive paper on communications and community connections is planned for later in the year and will include the bottled water options.

- The content of the Water Supply Section of the Wellington Regional Council Internet site was fully reviewed.  New and revised/updated material was written, and will be added to the site during April.

5.4	Economics

- The new wholesale water database has now been running for approximately six months.  Minor teething problems have been fixed and an instruction manual complied.

- A time dependent database package suitable for the storage of data from the telemetry system has been selected and is currently being implemented.

- A new contract for the supply of electricity was negotiated between the Council and TrustPower, and was implemented in October 1999.  In-depth analysis is currently being done in conjunction with implementation of the pumping station optimiser to try and minimise network costs.

6.	Projects undertaken by Engineering Consultancy for the Strategy and Asset Group

### Te Marua Lakes to Treatment Plant Pipelines

The Contractor, C M Contracting Ltd, is making preparations for the cement mortar lining of the relaid bitumen lined pipes.  Work will start on-site in early March 2000.

- Kaitoke Weir Repair

The Contract for repairing the concrete surface of the Kaitoke weir was awarded to Works Infrastructure Ltd.  Approximately 90 percent of the work has been completed.  The recent rain and high river flows are delaying the completion of the work

- Kaitoke Concrete Pipeline

An internal inspection has been carried out on the concrete pipeline between the Kaitoke Flume Bridge and the entrance to No. 2 Tunnel.  The pipeline was found to be generally in reasonable condition.  A report is being prepared recommending remedial works to the joints and eroded areas.

- Branch Line to Plateau Reservoir

Upper Hutt City Council has requested a direct connection from the Kaitoke main to the Plateau Reservoir at Te Marua.  The route of this proposal pipeline is being investigated.

- Silverstream Scour on Kaitoke Main

Options are being investigated for installing a drainage pipeline to facilitate draining the Kaitoke main at Silverstream.

- OK Main Slip Lining : Waiapu Road to The Rigi

A 300 m section of the OK main between The Rigi and Waiapu Road (through the Karori Tunnel) has been slip lined with a 400 mm diameter polyethylene pipe.  The Contract achieved Practical Completion on 27 January 2000.  The Contract is now in the maintenance period.

- OK Main Cement Mortar Lining : Thorndon to Karori

The Contract Documents for the cement mortar lining of the OK main between Thorndon and Karori are being prepared.

- OK Main Crossing of Korokoro Stream

The OK main between Randwick and Korokoro supplies water to the new Rahui Reservoir.  The pipe crossing the Korokoro Stream is corroded and poorly supported.  It could fail during a moderate earthquake.  The options for replacing this crossing are being considered.

- Waterloo Capacity Increase

The new Wellington pumps continue to work satisfactorily.  This project is complete.

###### Plimmerton/Pukerua Bay Branch Pipeline Shut-off Valve

The valve chamber and shut-off valve have been installed.  Arrangements are being made to commission the automatic control of the valve.

- Hutt Estuary Bridge Pipelines

Details of the strengthening work on the Hutt Estuary Bridge have been received from Hutt City Council.  Quotations are being requested for the supply of flexible couplings for our pipelines to accommodate the design movement of the bridge in a seismic event.

- Buick Street Pumping Station Decommissioning

Arrangements are being made to plug the bores and remove the pumping station building.

###### Wainuiomata River Bridge

The Contract for removal of the old deck and strengthening of the abutments and central pier is in the maintenance period.

#### Karori Reservoir Rationalisation

All major pipework alterations are complete and the site has been cleaned up.  A number of outstanding items will be attended to in April 2000.

- Haywards Reservoir Utilisation

New control valves and pipework are proposed for Haywards Reservoir.  This is to allow remote control, turnover in the reservoir to maintain water quality and greater utilisation of the available water storage.  Construction drawings are being prepared and the installation is programmed for April/ May 2000.

- Water Meter Replacement Programme

The programme of replacing the existing revenue meters is progressing satisfactorily.  Eleven meters have so far been installed this financial year.  Nine more meters are programmed to be installed by the end of June 2000.

Engineering Consultancy Group

(January/February 2000)

Engineering Consultancy Group

Review of Operations for the Period Ended 29 February 2000

1.	Work carried Out for the Strategy and Asset Group

The main capital projects for which the Engineering Consultancy Group has responsibility are itemised in the Strategy and Asset Group report.  Support is also provided for other projects being undertaken by this group.

2.	Work carried Out for the Operations Group

The Engineering Consultancy Group has continued to provide support for smaller projects arising from the operation and maintenance of the wholesale water supply system.

3.	Work carried Out for Wellington City Council

3.1	General

Current projects underway are detailed in the following sections.

3.2	Pipeline Projects

Tenders were awarded for the replacement of water mains for two difficult inner city projects.  These are Manners Street, from Cuba to Willis Street, and Cuba Street, from Ghuznee to Webb Street.  Both of these projects are nearing completion.

Contract documentation preparation for main laying in Rolleston Street, Salisbury Avenue, Salisbury Terrace and adjustment to the Bell Road Zone is complete, and tenders are about to be invited.

3.3	Grenada North High Level Reservoir

This permanent reservoir, 150 m³ capacity, will replace the Grenada North temporary tanks.  The site is at a higher level to the east of Nassau Avenue on land that has recently been transferred from TransPower to Wellington City Council.  The intention of this reservoir and associated pipework is the second stage in the upgrade of the Grenada North water supply following the contamination incident in early 1998.

The design report has been prepared and approved, along with a draft resource consent application.

3.4	Wadestown Reservoir

Montgomery Watson Ltd was engaged for the design of a replacement reservoir, capacity 1,800 m³, along with the obtaining of resource consents necessary for the completion of the reservoir on the Town Belt, as well as for access across the Town Belt.

The resource consent has been obtained, with the conditions being much more stringent than expected.  The requirement that the reservoir be totally buried and the surface contoured has been investigated, with alternative designs prepared.

3.5	Karori South Reservoir

Approval has been received for a project to create the new larger zone and to allow the decommissioning of the Allington Road Pumping Station and removal of the associated precast concrete tanks.  This involves main laying to connect the two parts of the zone.

3.6	Eastern Suburbs Storage1

There is a storage deficit in the Low Level Zone of 10 ML.  This was identified and reported on at the time of approval of the Macalister Park 20 ML Reservoir.  Of this storage, approximately 7 ML is required in the Eastern Suburbs (Miramar) and 3 ML in the Southern Suburbs (Island Bay).

Because these reservoirs will balance on the Low Level Zone, a very careful analysis is required to establish the optimum reservoir levels.  Additional pressure monitoring points have been established at the Moa Point Sewage Treatment Plant and Kilbirnie Crescent.  Network modelling was undertaken to establish levels for the reservoir at different sites, as well as enhancement required to the pipe network.

Detailed information has been received on the potential sites, which are being assessed.

3.7	Work Related to the Facilities Management Contract

The maintenance of the Wellington City Council plan record system continues but advice has been received that this service will not be required after 30 June 2000.

Subdivisions are assessed for compliance with the Code of Practice for Land Development and approval given.

Project Information Memoranda (PIMs) and Land Information Memoranda (LIMs) are processed on a regular basis for the City Council.

4.	Other Projects

4.1	Rallywood Bridge

This bridge project for the Plantation Forestry Department has been investigated, designed and tenders invited.  A tender recommendation was made but the Contract will not be awarded until various agreements have been completed.

4.2	Waterloo Car Parks

An investigation is underway to fit in some more parking spaces at the Waterloo Bus/Rail Interchange and prices have been obtained.

Laboratory Services

(January/February 2000)

Laboratory Services Department

Review of Operations for the Period Ended 29 February 2000

1.	Items of Note

- Summer sampling will be ending on 31 March 2000.

- Giardia and Cryptosporidium in small numbers were again detected at Wainuiomata River intake.  The numbers are low and appear to be consistent with the trend for this area.

- Algae numbers have dropped in the Te Marua Lakes.

- The new LIMS is up and running.  Staff members are being trained on the job and there is a facility to access results through a web page.

2.	Financial

The operating surplus is below budget at this stage.  Although operating expenditure is slightly under budget currently, the reduced level of internal revenue significantly outweighs any direct cost savings.

3.	Business Summary

3.1	Quality

There were no requests for retesting samples and test reports are being sent out within the agreed time frames.

3.2	Health and Safety

There are no incidents to report.

3.3	Number of Samples Analysed

| January | February |
| --- | --- |
| Samples 976 Approximate tests 3,970 | Samples 1,118 Approximate tests 4,200 |

Plantation Forestry

(January/February 2000)

Plantation Forestry Department

Review of Operations for the Period Ended 29 February 2000

1.	Log Harvest Contract

February was a further good month, with a total of 5,901 tonnes for a net revenue of $199,609.

Recent grade outputs have been:

|  | November 1999 |  | December 1999 |  | January 2000 |  | February 2000 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Grade | Tonnes | % | Tonnes | % | Tonnes | % | Tonnes | % |
| Pruned domestic | 306.00 | 4.27 | 1,337.86 | 5.64 | 25.07 | 0.55 | 83.81 | 1.42 |
| Pruned export | 82.04 | 1.14 | 179.57 | 3.00 | 0.00 | 0.00 | 0.00 | 0.00 |
| Partial pruned | 375.44 | 5.24 | 232.54 | 3.88 | 0.00 | 0.00 | 214.04 | 3.63 |
| S Grade | 905.24 | 12.63 | 863.63 | 14.41 | 875.91 | 19.25 | 1,363.71 | 23.11 |
| A Grade | 323.34 | 4.51 | 344.40 | 5.75 | 400.91 | 8.81 | 506.83 | 8.59 |
| L Grade | 652.69 | 9.10 | 495.11 | 8.26 | 467.34 | 10.27 | 554.53 | 9.41 |
| R Grade | 114.95 | 1.60 | 117.67 | 1.96 | 0.00 | 0.00 | 0.00 | 0.00 |
| K Sawlog | 1,721.49 | 24.01 | 1,488.70 | 24.84 | 1,450.39 | 31.87 | 1,417.36 | 24.02 |
| K Rough | 590.43 | 8.24 | 341.72 | 5.70 | 65.14 | 1.43 | 284.38 | 4.82 |
| Pulp | 1,679.14 | 23.42 | 1,271.07 | 21.20 | 958.46 | 21.06 | 1,338.01 | 22.67 |
| O/S Pulp | 404.69 | 5.65 | 311.88 | 5.20 | 307.54 | 6.76 | 404.69 | 5.65 |
| Other | 13.27 | 0.19 | 10.16 | 0.17 | 0.00 | 0.00 | 13.27 | 0.19 |
|  | 7,168.74 |  | 5,994.29 |  | 4,550.75 |  | 5,901.33 |  |

Over these four months Pakuratahi has produced 1,836 tonnes of pruned and partial pruned logs for a gross return of $228,518, further demonstrating the improved returns available from a full silvicultural regime.

Domestic prices have remained stable for the month and the only increase in export has been the introduction of two new sawlog grades at $89.65 and $73.04, both of which have been suitable for the logs from Pakuratahi.  One pleasing aspect is that for two settings we now receive a positive contribution for pulp logs. This follows four years of negative returns.  A further increase of $1.50 per tonne would see all pulp output from Pakuratahi making a positive contribution but nearly $5.50 would be required for oversized pulp.

The relatively fine weather has allowed continuing logging and resulted in little maintenance on the roads.  The crews are now concentrating on clearfelling those ground based areas which will be unsuitable for winter logging.  This has delayed the start on logging the area to the east of the walkway so we hope for a dry autumn.

One of the ground based crew bosses has just purchased a lightweight hauler designed for small piece size and for easy relocation.  As soon as this is delivered the more weather prone hauler blocks can be started and a programme developed for logging through the winter.

2.	Silviculture Contracts

One hundred and sixty-two hectares of a total 306 hectares of the current year’s contract have been completed.  One of the contractors is in financial difficulties and may not be able to complete his assigned block.  If necessary, we will have the block completed by one of the other contractors.

3.	Plantation Forestry Operations

The regular rain has ensured continuing growth among the new plantings.

Foliage samples were taken from selected blocks in early February and the initial analysis of these shows the trees to be in better health than previously thought. When all the results are in we will develop a fertilising programme to overcome the soil deficiencies detected.

Earlier in the season we had sprayed the Douglas fir stands adjacent to the Pakuratahi River for weed competition.  Observations show little effect on the weed growth and the contractor has agreed to respray at their and the chemical company’s cost.  This work will be done as soon as a suitable period of dry weather occurs.

Three logging crews and three silvicultural crews to be supervised combined with staff sickness has resulted in a busy month.

4.	Forest Access

Maungakotukutuku remains the only access problem but this is not serious as no work is programmed in the near future.

The new road into Pakuratahi East continues to be satisfactory with no major problems.  Millings are to be placed on the State Highway 2 end of the road to prevent the trucks tracking metal onto the highway.  The logging truck drivers have also been requested to stop short of the entrance to check their tie-down chains and this should reduce the bark debris around the entrance.  Most of the major roading within the block has been completed and stabilised so there are only the access tracks into each block and the maintenance to be carried out in  future.

As yet, we have still been unable to finalise the agreement with the Rallywoods Partnership for reciprocal access.  We are now in a position where agreement has been reached with M Bradley and Craig’s Flat but one of the partners of Rallywoods has decided to sell out of the partnership.  Hopefully this will not lead to an excessive delay, as the successful tenderer for the construction of the bridge is ready to start and work in the river cannot continue after 31 May because of spawning.

Approximately 7 km of the Puketiro road has been upgraded by widening and reshaping of water tables.  There is about a further 5 km to be done next summer. The Engineering Consultancy Group has been engaged to design and cost a concrete ford to replace the unformed ford on the Wainui Stream.  Resource consents will be sought for this construction to take place next spring after spawning.  This will only leave the first 400 m of Cook Road to be upgraded and the access tracks to the blocks to be harvested.

5.	Market Trends

Export markets are levelling out, with any price gains coming from currency fluctuations.  Domestic demand for the better sawlogs grades is particularly strong and modest price increases are anticipated for the next quarter commencing April.

Although roundwood mills have shown interest in the Corsican stands, to date no deals have been done.  Past practice has been for the roundwood company to fell their own product but if arrangements cannot be completed it may be better to have the contract crews fell the trees and to sell it “at the mill gate”